## cost estimate
Account | Account Title | FOAK Estimated Cost ($2025) | NOAK Estimated Cost ($2025) | FOAK Estimated Cost std ($2025) | NOAK Estimated Cost std ($2025) | FOAK LCOE | NOAK LCOE | FOAK LCOE_std | NOAK LCOE_std
10 | Capitalized Pre-Construction Costs | 39000965 | 17383432 | 6428647 | 2050173 | 57 | 25 | 9 | 3
11 | Land Cost | 78744 | 78744 | 10890 | 10890 | 0 | 0 | 0 | 0
12 | Site Permits | 69765 | 69765 | 10216 | 10216 | 0 | 0 | 0 | 0
13 | Plant Licensing | 27967992 | 6350458 | 6230087 | 1414614 | 40 | 9 | 9 | 2
14 | Plant Permits | 4819462 | 4819462 | 909421 | 909421 | 7 | 7 | 1 | 1
15 | Plant Studies | 6065001 | 6065001 | 1112848 | 1112848 | 8 | 8 | 1 | 1
20 | Capitalized Direct Costs | 101199731 | 46936754 | 16313059 | 10259642 | 148 | 68 | 23 | 15
21 | Structures and Improvements | 13432689 | 3177691 | 6372514 | 1140090 | 19 | 4 | 9 | 1
211 | Site Preparation/ Yard Work | 199630 | 114719 | 20187 | 11600 | 0 | 0 | 0 | 0
211.1 | Cleaning and Grubbing | 116503 | 66950 | 17767 | 10210 | 0 | 0 | 0 | 0
211.2 | Stripping Topsoil | 68303 | 39251 | 11377 | 6537 | 0 | 0 | 0 | 0
211.3 | Excavation | 14823 | 8518 | 2049 | 1178 | 0 | 0 | 0 | 0
212 | Reactor Island Civil Structures | 1769051 | 1016604 | 364997 | 209749 | 2 | 1 | 0 | 0
212.1 | Reactor Building Slab Roof | 195598 | 112402 | 29949 | 17210 | 0 | 0 | 0 | 0
212.2 | Reactor Building Basement | 154555 | 88817 | 23486 | 13496 | 0 | 0 | 0 | 0
212.3 | Reactor Building Walls | 163360 | 93876 | 23880 | 13723 | 0 | 0 | 0 | 0
212.4 | Reactor Building Liner | 1115473 | 641018 | 347904 | 199926 | 1 | 0 | 0 | 0
212.5 | Reactor Building HVAC | 140062 | 80488 | 97066 | 55780 | 0 | 0 | 0 | 0
213 | Main Function Buildings | 51770 | 29750 | 4854 | 2789 | 0 | 0 | 0 | 0
213.1 | Energy conversion Building | 51770 | 29750 | 4854 | 2789 | 0 | 0 | 0 | 0
213.11 | Energy Conversion Building Slab Roof | 16127 | 9268 | 2284 | 1312 | 0 | 0 | 0 | 0
213.12 | Energy Conversion Building Basement | 12522 | 7196 | 1773 | 1019 | 0 | 0 | 0 | 0
213.13 | Energy Conversion Building Walls | 23120 | 13286 | 3786 | 2175 | 0 | 0 | 0 | 0
214 | Buildings to Support Main Function | 11412237 | 2016616 | 6371253 | 1125842 | 16 | 2 | 9 | 1
214.7 | Emergency and Start-up Power Systems Building | 11412237 | 2016616 | 6371253 | 1125842 | 16 | 2 | 9 | 1
214.72 | Diesel Generator | 11412237 | 2016616 | 6371253 | 1125842 | 16 | 2 | 9 | 1
22 | Reactor System | 40711806 | 14296881 | 4410131 | 1595668 | 59 | 20 | 6 | 2
221 | Reactor Components | 25891602 | 6347730 | 4219089 | 1075583 | 37 | 9 | 6 | 1
221.1 | Reactor Vessel and Accessories | 21782334 | 5621596 | 4077515 | 1052327 | 31 | 8 | 5 | 1
221.11 | Reactor Support | 3295580 | 850524 | 697657 | 180051 | 4 | 1 | 1 | 0
221.13 | Inner Vessel Structure - stainless_steel | 18486754 | 4771071 | 3691507 | 952706 | 27 | 6 | 5 | 1
221.3 | Non-Fuel Core Internals | 4109267 | 726134 | 532658 | 94124 | 6 | 1 | 0 | 0
221.31 | Reflector | 314962 | 55655 | 36940 | 6527 | 0 | 0 | 0 | 0
221.311 | Radial Reflector - Graphite | 237517 | 41970 | 34670 | 6126 | 0 | 0 | 0 | 0
221.312 | Axial Reflector - Graphite | 77445 | 13685 | 12333 | 2179 | 0 | 0 | 0 | 0
221.32 | Shield | 122415 | 21631 | 22845 | 4037 | 0 | 0 | 0 | 0
221.322 | Out The Vessel Shield Materials - WEP | 122415 | 21631 | 22845 | 4037 | 0 | 0 | 0 | 0
221.33 | Moderator - Graphite | 351307 | 62078 | 50038 | 8842 | 0 | 0 | 0 | 0
221.34 | Moderator (Booster) - ZrH | 3320581 | 586768 | 532788 | 94147 | 4 | 0 | 0 | 0
222 | Main Heat Transport System | 2320844 | 425242 | 241303 | 42996 | 3 | 0 | 0 | 0
222.1 | Fluid Circulation Drive System | 1565852 | 276696 | 216996 | 38344 | 2 | 0 | 0 | 0
222.13 | Compressor - GCMR | 1565852 | 276696 | 216996 | 38344 | 2 | 0 | 0 | 0
222.2 | Reactor Heat Transfer Piping System - GCMR | 372776 | 65871 | 51966 | 9182 | 0 | 0 | 0 | 0
222.3 | Heat Exchangers | 363832 | 64291 | 52195 | 9223 | 0 | 0 | 0 | 0
222.31 | Primary Heat Exchanger - SS316 | 363832 | 64291 | 52195 | 9223 | 0 | 0 | 0 | 0
222.5 | Initial Coolant Inventory - Helium | 18382 | 18382 | 2950 | 2950 | 0 | 0 | 0 | 0
223 | Safety Systems | 2518784 | 445085 | 273799 | 48382 | 3 | 0 | 0 | 0
223.2 | Reactor Cavity Cooling System (Rvacs) | 2518784 | 445085 | 273799 | 48382 | 3 | 0 | 0 | 0
223.21 | Rvacs (Cooling Vessel) | 1217643 | 215165 | 189361 | 33461 | 1 | 0 | 0 | 0
223.22 | Rvacs (Intake Vessel) | 1301140 | 229920 | 202888 | 35851 | 1 | 0 | 0 | 0
227 | Reactor Instrumentation and Control (I&C) | 9944133 | 7072383 | 1858540 | 1321815 | 14 | 10 | 2 | 1
228 | Reactor Plant Miscellaneous Items | 36441 | 6439 | 8320 | 1470 | 0 | 0 | 0 | 0
23 | Energy Conversion System | 19351082 | 13762714 | 14067156 | 10004725 | 28 | 20 | 20 | 14
232 | Energy Applications | 18177914 | 12928343 | 14055912 | 9996727 | 26 | 18 | 20 | 14
232.1 | Electricity Generation Systems | 18177914 | 12928343 | 14055912 | 9996727 | 26 | 18 | 20 | 14
236 | Common Instrumentation & Controls | 1173168 | 834371 | 265577 | 188881 | 1 | 1 | 0 | 0
24 | Electrical Equipment | 10822322 | 7696961 | 3179801 | 2261511 | 15 | 11 | 4 | 3
241 | Switchgear | 1056879 | 751665 | 596654 | 424347 | 1 | 1 | 0 | 0
242 | Station Service Equipment | 791487 | 562915 | 536551 | 381601 | 1 | 0 | 0 | 0
243 | Switchboards | 253555 | 180331 | 122233 | 86934 | 0 | 0 | 0 | 0
244 | Protective Equipment | 829509 | 589957 | 465980 | 331410 | 1 | 0 | 0 | 0
245 | Electrical Structure & Wiring Container | 4676934 | 3326290 | 2267372 | 1612581 | 6 | 4 | 3 | 2
246 | Power & Control Wiring | 3213954 | 2285802 | 2169913 | 1543267 | 4 | 3 | 3 | 2
25 | Initial Fuel Inventory | 16881829 | 8002505 | 1840147 | 1160601 | 24 | 11 | 2 | 1
251 | First Core Mining | 3630085 | 3630085 | 608719 | 608719 | 5 | 5 | 0 | 0
252 | First Core Conversion | 291704 | 291704 | 43939 | 43939 | 0 | 0 | 0 | 0
253 | First Core Enrichment | 2174913 | 2174913 | 956769 | 956769 | 3 | 3 | 1 | 1
254 | First Core Fuel Assembly Fabrication - Yes | 10785126 | 1905801 | 1639102 | 289640 | 15 | 2 | 2 | 0
30 | Capitalized Indirect Services Cost | 8203844 | 4107110 | 1207976 | 592168 | 12 | 6 | 1 | 0
31 | Factory & field indirect costs | 2402935 | 1021302 | 518545 | 330147 | 3 | 1 | 0 | 0
32 | Factory and construction supervision | 841875 | 236045 | 554549 | 136476 | 1 | 0 | 0 | 0
33 | Startup Costs | 2785469 | 1600699 | 533923 | 306825 | 4 | 2 | 0 | 0
34 | Shipping and Transportation Costs | 980883 | 563675 | 248860 | 143010 | 1 | 0 | 0 | 0
35 | Engineering Services | 708844 | 407345 | 152167 | 87444 | 1 | 0 | 0 | 0
36 | PM/CM Services | 483836 | 278041 | 100253 | 57611 | 0 | 0 | 0 | 0
40 | Capitalized training costs | 171948 | 171948 | 44672 | 44672 | 0 | 0 | 0 | 0
41 | staff recruitment and training | 171948 | 171948 | 44672 | 44672 | 0 | 0 | 0 | 0
60 | Capitalized Financial Costs | 2564406 | 1184012 | 324417 | 192722 | 3 | 1 | 0 | 0
62 | Interest | 2564406 | 1184012 | 324417 | 192722 | 3 | 1 | 0 | 0
70 | Annualized O&M Cost | 8465404 | 4784421 | 795117 | 494426 | 165 | 93 | 15 | 9
71 | O&M Staff | 2852574 | 2852574 | 341169 | 341169 | 55 | 55 | 6 | 6
711 | Operators | 1855161 | 1855161 | 321375 | 321375 | 36 | 36 | 6 | 6
713 | Security Staff | 997412 | 997412 | 150627 | 150627 | 19 | 19 | 2 | 2
73 | Regulatory Costs | 126 | 28 | 25 | 5 | 0 | 0 | 0 | 0
75 | Capital Plant Expenditures | 5427706 | 1846946 | 691087 | 321111 | 105 | 36 | 13 | 6
752 | Annualized Inner Vessel Structure Replacements | 2639188 | 681123 | 527003 | 136009 | 51 | 13 | 10 | 2
753 | Annualized Moderator Replacements | 85957 | 15189 | 12243 | 2163 | 1 | 0 | 0 | 0
754 | Annualized Reflector Replacements | 44964 | 7945 | 5273 | 931 | 0 | 0 | 0 | 0
757 | Annualized Moderator Booster Replacements | 812479 | 143570 | 130362 | 23035 | 15 | 2 | 2 | 0
759 | Annualized Plant Maintenance (Misc.) | 1845115 | 999118 | 492309 | 313032 | 36 | 19 | 9 | 6
759.1 | Annualized Building and Structural Maintenance (Accounts 212–215) | 396991 | 91889 | 191201 | 34215 | 7 | 1 | 3 | 0
759.2 | Annualized Main Heat Transport System Maintenance (Accounts 222.1–222.3 and 222.6) | 69073 | 12205 | 7229 | 1277 | 1 | 0 | 0 | 0
759.3 | Annualized Safety System Maintenance (Account 223) | 75563 | 13352 | 8213 | 1451 | 1 | 0 | 0 | 0
759.4 | Annualized Reactor Plant Equipment Maintenance (Accounts 221.11, 226, and 228) | 99960 | 25708 | 20966 | 5407 | 1 | 0 | 0 | 0
759.5 | Annualized Reactor I&C Maintenance (Account 227) | 298324 | 212171 | 55756 | 39654 | 5 | 4 | 1 | 0
759.6 | Annualized Energy Conversion System Maintenance (Account 23) | 580532 | 412881 | 422014 | 300141 | 11 | 8 | 8 | 5
759.7 | Annualized Electrical Equipment Maintenance (Account 24) | 324669 | 230908 | 95394 | 67845 | 6 | 4 | 1 | 1
78 | Annualized Decommissioning Cost | 184996 | 84871 | 23716 | 14165 | 3 | 1 | 0 | 0
80 | Annualized Fuel Cost | 4130644 | 1958052 | 450247 | 283975 | 80 | 38 | 8 | 5
82 | Additional Nuclear Fuel | 4130644 | 1958052 | 450247 | 283975 | 80 | 38 | 8 | 5
OCC | Overnight Capital Cost | 148576489 | 68599244 | 18796068 | 11165954 | - | - | - | -
OCC per kW | Overnight Capital Cost per kW | 24762 | 11433 | 3132 | 1860 | - | - | - | -
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 131694659 | 60596739 | 18774399 | 11245496 | - | - | - | -
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 21949 | 10099 | 3129 | 1874 | - | - | - | -
TCI | Total Capital Investment | 151140896 | 69783257 | 19120486 | 11358676 | - | - | - | -
TCI per kW | Total Capital Investment per kW | 25190 | 11630 | 3186 | 1893 | - | - | - | -
AC | Annualized Cost | 12596048 | 6742473 | 908498 | 553197 | - | - | - | -
AC per MWh | Annualized Cost per MWh | 245 | 131 | 17 | 10 | - | - | - | -
LCOE | Levelized Cost Of Energy ($/MWh) | 467 | 233 | 41 | 24 | - | - | - | -
LCOH | Levelized Cost Of Heat ($/MWth) | 165 | 83 | 14 | 8 | - | - | - | -

## servicing campus cost estimate
Account | Account Title | Estimated Cost ($ 2025) | Estimated Cost std ($ 2025) | LCOE Contribution ($/MWh)
10 | Capitalized Pre-Construction Costs | 156215644 | 15180031 | 0
11 | Land Cost | 2400092 | 362687 | 0
12 | Site Permits | 2717253 | 425601 | 0
13 | Plant Licensing | 85584393 | 10724195 | 0
14 | Plant Permits | 5067233 | 1042816 | 0
15 | Plant Studies | 60446670 | 11408876 | 0
20 | Capitalized Direct Costs | 12874920995 | 3607357689 | 18
21 | Structures and Improvements | 8602351201 | 3615704429 | 12
211 | Site Preparation/ Yard Work | 33841095 | 5610317 | 0
211.1 | Cleaning and Grubbing | 3492724 | 539718 | 0
211.2 | Stripping Topsoil | 2118083 | 312089 | 0
211.4 | Roads | 9464763 | 4600669 | 0
211.9 | Security Fencing | 18765523 | 2772723 | 0
211.91 | Security Fencing Limited | 363042 | 54671 | 0
211.93 | Security Fencing Protected | 18402480 | 2776155 | 0
214 | Servicing Facilities Structures | 8557910106 | 3617356132 | 12
214.1 | Servicing Building | 1084327472 | 374983527 | 1
214.11 | Servicing Hot Cell Building Structure | 1084327472 | 374983527 | 1
214.2 |  | 20310641 | 7327777 | 0
214.21 | Helium Purification and Storage Building Structure | 20310641 | 7327777 | 0
214.3 | Control Buidlings | 63811025 | 19719653 | 0
214.31 | Local Control Building Structure | 32593420 | 14829443 | 0
214.32 | Remote Control Center Structure | 31217604 | 12687319 | 0
214.4 | Radioactive Waste Processing Building | 29212512 | 10879518 | 0
214.41 | Radioactive Waste Processing Building Structure | 29212512 | 10879518 | 0
214.6 | Used Fuel Storage Pads | 1552533473 | 513295585 | 2
214.7 | Rad Waste Storage Warehouses | 5807714980 | 3631248454 | 8
215 | Air Tranport Hangar | 10600000 | 0 | 0
215.1 | Air Transport Hangar | 10600000 | 0 | 0
22 | Main Facilities Estimated As Wholes | 270308849 | 112616325 | 0
221 | Reactor Cask Management Yard and Inspection Shop | 12134642 | 1837498 | 0
222 | Vehicle Depot and Mechanic Shop | 38552884 | 5399884 | 0
224 | Parts Service Center and Warehouse | 16473752 | 8217692 | 0
225 | Administrative Building | 203147570 | 112947241 | 0
23 | Equipment | 3342582760 | 19239216 | 4
23.1 | Servicing Hot Cell | 2086666666 | 0 | 3
23.2 | Helium Purification Equipment | 468387 | 200304 | 0
23.4 | Radioactive Waste Processing Hot Cell | 1060000000 | 0 | 1
23.5 | Local Integrated Control Rooms | 72723491 | 0 | 0
23.6 | Remote Control Rooms | 112290881 | 19243863 | 0
23.8 | Reactor Transport Casks | 10433333 | 0 | 0
28 | Auxiliary Infrastructure Equipment | 659678182 | 49929368 | 0
281 | Emergency Power | 137354612 | 35356194 | 0
282 | Service Air Water Building | 45270900 | 0 | 0
283 | Fire Station | 43630650 | 0 | 0
284 | Security Building | 10991433 | 4180713 | 0
285 | Switchyard | 128018189 | 18468012 | 0
286 | Onsite Transport Equipment | 4395964 | 683367 | 0
286.1 | Local Reactor Transport Vehicles | 2221379 | 472684 | 0
286.2 | Utility Vehicles | 2174584 | 457425 | 0
287 | Offsite Transport Equipment | 207602865 | 30777114 | 0
287.1 | Reactor Transport Vehicles | 12413791 | 2948476 | 0
287.2 | Helium Transport Trucks | 42524707 | 9067821 | 0
287.3 | Water Tanker Trucks | 24795162 | 5393237 | 0
287.4 | Maintenance Trucks | 4815998 | 1070788 | 0
287.5 | Air Transport Equipment | 123053204 | 29726486 | 0
287.51 | Heavy Lift Helicopters | 121851712 | 29734373 | 0
287.52 | Aircraft Maintenance Equipment | 1201492 | 254388 | 0
288 | Dispered Infrastructure | 82413566 | 9091979 | 0
288.1 | Communication | 6594201 | 953644 | 0
288.2 | Security Cameras | 18195404 | 4468623 | 0
288.3 | Motion Detectors | 24475238 | 4947350 | 0
288.4 | Guard Station | 30804415 | 6604616 | 0
288.5 | Radiation Monitors | 2344307 | 560691 | 0
30 | Capitalized Indirect Services Cost | 6437460497 | 1803678844 | 9
40 | Capitalized training costs | 339310 | 77371 | 0
41 | staff recruitment and training | 339310 | 77371 | 0
60 | Capitalized Financial Costs | 1050271949 | 291855755 | 1
62 | Interest | 1050271949 | 291855755 | 1
70 | Annualized O&M Cost | 2792915906 | 596298297 | 54
71 | O&M Staff | 1617630869 | 576479426 | 31
711 | Operators | 33553320 | 12143762 | 0
712 | Remote Monitoring Technicians | 70610084 | 26510363 | 1
713 | Security Staff | 28529282 | 8594985 | 0
714 | Maintenance Staff | 1246661473 | 532267974 | 24
715 | Engineering Staff | 97934304 | 16297821 | 1
716 | Continuing Education and Staff Retraining | 29545769 | 10529304 | 0
717 | Management Staff | 110796634 | 39484892 | 2
74 | Fixed O&M Utilities and Materials | 1175285036 | 91592255 | 22
741 | Operating Chemicals and Lubricants | 64374604 | 18036788 | 1
742 | Spare Parts | 182456569 | 2374489 | 3
743 | Utilities except electricity, Supplies, and Consumables | 128749209 | 36073576 | 2
744 | Electricity | 94017504 | 14451059 | 1
747.1 | Annualized Transportation Costs | 18779019 | 2702026 | 0
747.2 | Annualized Cask Replacements | 255622764 | 34726404 | 4
747.21 | Used Fuel Cask | 94770492 | 11171228 | 1
747.22 | Reactor Transport Cask | 42057662 | 0 | 0
747.23 | Radwaste Storage Cask | 54443177 | 5162785 | 1
747.24 | Used Fuel Storage Additional Overpacks | 64351431 | 32692560 | 1
747.3 | Annualized Helium Replenishment | 3648726 | 619276 | 0
747.4 | Annualized Other Supplies and Utilities | 64374604 | 18036788 | 1
747.5 | Servicing Vehicle O&M | 363262033 | 45482367 | 7
747.51 | Reactor Transport Vehicles O&M | 99625535 | 22977516 | 1
747.52 | Helium Transport Trucks O&M | 113578644 | 26650526 | 2
747.53 | Water Tanker Trucks O&M | 101849860 | 22068616 | 1
747.54 | Maintenance Trucks O&M | 48207992 | 10223776 | 0
OCC | Overnight Capital Cost | 19468936447 | 5410142732
OCC per reactor | Overnight Capital Cost per Operating Reactor | 20009184 | 5560270
TCI | Total Capital Investment | 20519208397 | 5701998488
TCI per reactor | Total Capital Investment per Operating Reactor | 21088600 | 5860224
Annual Cost | Annual Servicing Campus Cost | 2792915906 | 596298297
Annual Cost per reactor | Annual Servicing Campus Cost per Operating Reactor | 2870417 | 612845
LCOE | Servicing Campus Contribution to Fleet LCOE ($/MWh) | 84 | 15

## manufacturing campus cost estimate
Account | Account Title | Estimated Cost ($ 2025) | Estimated Cost std ($ 2025) | LCOE Contribution ($/MWh)
10 | Capitalized Pre-Construction Costs | 150389090 | 15167413 | 0
11 | Land Cost | 276183 | 46208 | 0
12 | Site Permits | 17826 | 2915 | 0
13 | Plant Licensing | 86337598 | 10959906 | 0
14 | Plant Permits | 5024306 | 1075314 | 0
15 | Plant Studies | 58733175 | 12065050 | 0
20 | Capitalized Direct Costs | 268439481 | 26059378 | 0
21 | Structures and Improvements | 30637969 | 4899077 | 0
211 | Site Preparation/ Yard Work | 29382631 | 4925347 | 0
211.1 | Cleaning and Grubbing | 416931 | 67800 | 0
211.2 | Stripping Topsoil | 246604 | 37666 | 0
211.4 | Roads | 9721196 | 3811078 | 0
211.9 | Security Fencing | 18997899 | 2798935 | 0
211.91 | Security Fencing Limited | 375748 | 54663 | 0
211.93 | Security Fencing Protected | 18622150 | 2804810 | 0
214 | Servicing Facilities Structures | 1255337 | 396470 | 0
214.3 | Control Buidlings | 1255337 | 396470 | 0
214.31 | Local Control Buidling Structure | 1255337 | 396470 | 0
22 | Main Facilities Estimated As Wholes | 159449265 | 25308513 | 0
221 | Manufacturing Building | 48322816 | 11789886 | 0
222 | Fueling Building | 25532895 | 6226247 | 0
223 | Testing Building | 29715297 | 3759213 | 0
224 | Warehouse | 14412942 | 6339084 | 0
225 | Administrative Building | 41465313 | 20104961 | 0
23 | Equipment | 18155636 | 0 | 0
23.5 | Local Integrated Control Rooms | 18155636 | 0 | 0
28 | Auxiliary Infrastructure Equipment | 60196609 | 4421024 | 0
281 | Emergency Power | 17497370 | 0 | 0
283 | Fire Station | 14543550 | 0 | 0
284 | Security Building | 11145693 | 4171736 | 0
285 | Switchyard | 2548228 | 1051465 | 0
286 | Onsite Transport Equipment | 2408374 | 563254 | 0
286.1 | Local Reactor Transport Vehicles | 2231266 | 563071 | 0
286.2 | Utility Vehicles | 177107 | 39442 | 0
288 | Dispered Infrastructure | 12053393 | 0 | 0
288.1 | Communication | 747679 | 0 | 0
288.2 | Security Cameras | 1933307 | 0 | 0
288.3 | Motion Detectors | 2598156 | 0 | 0
288.4 | Guard Station | 6774250 | 0 | 0
30 | Capitalized Indirect Services Cost | 134219740 | 13029689 | 0
40 | Capitalized training costs | 341879 | 69061 | 0
41 | staff recruitment and training | 341879 | 69061 | 0
60 | Capitalized Financial Costs | 29853207 | 2139796 | 0
62 | Interest | 29853207 | 2139796 | 0
70 | Annualized O&M Cost | 46536919 | 4919973 | 0
71 | O&M Staff | 21613388 | 4248026 | 0
711 | Operators (Testing Only) | 1610267 | 312465 | 0
712 | Warehouse Staff | 750403 | 165854 | 0
713 | Security Staff | 5267938 | 908268 | 0
714 | Maintenance Staff | 1047882 | 163344 | 0
715 | Engineering Staff (Testing Only) | 1796235 | 279756 | 0
716 | Continuing Education and Staff Retraining | 209454 | 20071 | 0
717 | Management Staff | 785454 | 75266 | 0
718 | Manfuacturing Building Staff | 6843587 | 3853384 | 0
719 | Fueling Building Staff | 3302164 | 1913346 | 0
74 | Fixed O&M Utilities and Materials | 24923531 | 2117413 | 0
741 | Operating Chemicals and Lubricants (Except Manufacturing and Fueling) | 1342197 | 130296 | 0
742 | Spare Parts (Except Manufacturing and Fueling) | 13421974 | 1302968 | 0
743 | Utilities except electricity, Supplies, and Consumables | 2684394 | 260593 | 0
744 | Electricity | 1219232 | 204910 | 0
745 | Manufacturing Building Equipment | 902181 | 388781 | 0
746 | Fueling Building Equipment | 210602 | 98546 | 0
747 | Other annual costs | 5142948 | 547991 | 0
747.1 | Annualized Transportation Costs | 872428 | 84692 | 0
747.3 | Annualized Helium Replenishment | 2928323 | 461820 | 0
747.4 | Annualized Other Supplies and Utilities | 1342197 | 130296 | 0
OCC | Overnight Capital Cost | 553390192 | 39665492
OCC per reactor | Overnight Capital Cost per Manufactured Reactor | 553390 | 39665
TCI | Total Capital Investment | 583243399 | 41805288
TCI per reactor | Total Capital Investment per Manufactured Reactor | 583243 | 41805
Annual Cost | Annual Manufacturing Campus Cost During Deployment | 46536919 | 4919973
Annual Cost per reactor | Annual Manufacturing Cost per Reactor Produced | 465369 | 49199
LCOE | Manufacturing Campus Contribution to Fleet LCOE ($/MWh) | 1 | 0

## fleet total cost estimate
Account | Account Title | Units | Reactor Fleet | Reactor Fleet std | Manufacturing Campus | Manufacturing Campus std | Servicing Campus | Servicing Campus std | Total Fleet | Total Fleet std
10 | Capitalized Pre-Construction Costs | $ 2025 | 17383432221 | 2050173318 | 150389090 | 15167414 | 156215645 | 15180031 | 17690036956 | 2050754036
20 | Capitalized Direct Costs | $ 2025 | 46936754617 | 10259642873 | 268439482 | 26059378 | 12874920995 | 3607357690 | 60080115094 | 11000057891
30 | Capitalized Indirect Services Cost | $ 2025 | 4107110030 | 592168902 | 134219741 | 13029689 | 6437460498 | 1803678845 | 10678790269 | 1853007175
40 | Capitalized Training Costs | $ 2025 | 171948115 | 44672537 | 341879 | 69061 | 339310 | 77371 | 172629305 | 44668934
60 | Capitalized Financial Costs | $ 2025 | 1184012166 | 192722610 | 29853207 | 2139796 | 1050271950 | 291855755 | 2264137323 | 354153013
70 | Annualized O&M Cost (Full-Fleet Deployment-Year Basis) | $ 2025 | 4784421006 | 494426899 | 46536920 | 4919974 | 2792915906 | 596298298 | 7623873832 | 732303005
80 | Annualized Fuel Cost | $ 2025 | 1958052255 | 283975952 | 0 | 0 | 0 | 0 | 1958052255 | 283975952
OCC | Overnight Capital Cost | $ 2025 | 68599244983 | 11165954136 | 553390192 | 39665493 | 19468936448 | 5410142733 | 88621571624 | 12544551074
OCC per reactor | Overnight Capital Cost per Reactor | $ 2025/reactor | 68599245 | 11165954 | 553390 | 39665 | 19468936 | 5410143 | 88621572 | 12544551
TCI | Total Capital Investment | $ 2025 | 69783257149 | 11358676746 | 583243400 | 41805289 | 20519208398 | 5701998488 | 90885708947 | 12852816419
TCI per reactor | Total Capital Investment per Reactor | $ 2025/reactor | 69783257 | 11358677 | 583243 | 41805 | 20519208 | 5701998 | 90885709 | 12852816
Annual Cost During Deployment | Full-Fleet Annual Cost During Deployment | $ 2025/year | 6742473262 | 553197047 | 46536920 | 4919974 | 2792915906 | 596298298 | 9581926087 | 773883343
Annual Cost per reactor During Deployment | Full-Fleet Annual Cost per Reactor During Deployment | $ 2025/reactor-year | 6742473 | 553197 | 46537 | 4920 | 2792916 | 596298 | 9581926 | 773883
Steady-State Annual Cost | Full-Fleet Steady-State Annual Cost After Deployment | $ 2025/year | 6742473262 | 553197047 | 0 | 0 | 2792915906 | 596298298 | 9535389168 | 774238862
Steady-State Annual Cost per reactor | Full-Fleet Steady-State Annual Cost per Reactor After Deployment | $ 2025/reactor-year | 6742473 | 553197 | 0 | 0 | 2792916 | 596298 | 9535389 | 774239
LCOE | Total Fleet Levelized Cost of Electricity | $/MWh | 233.76 | 24.73 | 1.9 | 0.14 | 106.09 | 21.52 | 341.75 | 31.9

## fleet annual cash flow
Year | Reactors Manufactured | Operating Reactors | Reactors Retiring at Year End | Servicing Events | Fleet Electricity Generation (MWh) | Reactor TCI Deployed | Reactor TCI Deployed std | Reactor Annual Cost | Reactor Annual Cost std | Manufacturing Campus TCI | Manufacturing Campus TCI std | Manufacturing Campus Annual Cost | Manufacturing Campus Annual Cost std | Servicing Campus TCI | Servicing Campus TCI std | Servicing Campus Annual Cost | Servicing Campus Annual Cost std | Total Fleet Cost | Total Fleet Cost std | Discount Factor | Discounted Fleet Cost | Discounted Fleet Cost std | Discounted Fleet Generation (MWh)
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583243400 | 41805289 | 0 | 0 | 20519208398 | 5701998488 | 0 | 0 | 21102451797 | 5698082190 | 1 | 21102451797 | 5698082190 | 0
1 | 100 | 0 | 0 | 0 | 0 | 6978325715 | 1135867675 | 0 | 0 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 0 | 0 | 7024862635 | 1135805037 | 0.93458 | 6565292182 | 1061500035 | 0
2 | 100 | 100 | 0 | 0 | 5123520 | 6978325715 | 1135867675 | 674247326 | 55319705 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 1904911233 | 591185079 | 9604021194 | 1250659147 | 0.87344 | 8388524058 | 1092374135 | 4475081
3 | 100 | 200 | 0 | 0 | 10247040 | 6978325715 | 1135867675 | 1348494652 | 110639409 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 1940305785 | 591373697 | 10313663072 | 1281532064 | 0.8163 | 8419021269 | 1046111903 | 8364637
4 | 100 | 300 | 0 | 0 | 15370560 | 6978325715 | 1135867675 | 2022741979 | 165959114 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 1975454937 | 591589483 | 11023059550 | 1314019988 | 0.7629 | 8409439353 | 1002459557 | 11726127
5 | 100 | 400 | 0 | 0 | 20494080 | 6978325715 | 1135867675 | 2696989305 | 221278819 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 2004425744 | 591632559 | 11726277683 | 1347962537 | 0.71299 | 8360673925 | 961078659 | 14611996
6 | 100 | 500 | 0 | 0 | 25617600 | 6978325715 | 1135867675 | 3371236631 | 276598523 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 2039312610 | 591909124 | 12435411875 | 1383350360 | 0.66634 | 8286240003 | 921784755 | 17070089
7 | 100 | 600 | 0 | 100 | 30741120 | 6978325715 | 1135867675 | 4045483957 | 331918228 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 2313123650 | 595647881 | 13383470242 | 1421135200 | 0.62275 | 8334552639 | 885011579 | 19144025
8 | 100 | 700 | 0 | 100 | 35864640 | 6978325715 | 1135867675 | 4719731283 | 387237933 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 2341828923 | 595779682 | 14086422841 | 1458923278 | 0.58201 | 8198426344 | 849106631 | 20873547
9 | 100 | 800 | 0 | 100 | 40988160 | 6978325715 | 1135867675 | 5393978609 | 442557638 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 2376501224 | 596163424 | 14795342468 | 1497881723 | 0.54393 | 8047686001 | 814748412 | 22294843
10 | 100 | 900 | 0 | 100 | 46111680 | 6978325715 | 1135867675 | 6068225936 | 497877342 | 0 | 0 | 46536920 | 4919974 | 0 | 0 | 2411122637 | 596583585 | 15504211207 | 1537865908 | 0.50835 | 7881554792 | 781773046 | 23440840
11 | 0 | 1000 | 0 | 100 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2445699358 | 597040424 | 9188172619 | 776618248 | 0.47509 | 4365234623 | 368965735 | 24341474
12 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.44401 | 4151203996 | 345845847 | 22749042
13 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.41496 | 3879629903 | 323220418 | 21260786
14 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.38782 | 3625822339 | 302075157 | 19869894
15 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.36245 | 3388619009 | 282313231 | 18569994
16 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.33873 | 3166933653 | 263844141 | 17355135
17 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.31657 | 2959751077 | 246583309 | 16219752
18 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.29586 | 2766122502 | 230451691 | 15158647
19 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.27651 | 2585161217 | 215375412 | 14166960
20 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.25842 | 2416038521 | 201285432 | 13240149
21 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.24151 | 2257979926 | 188117226 | 12373971
22 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.22571 | 2110261613 | 175810492 | 11564459
23 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.21095 | 1972207115 | 164308871 | 10807906
24 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.19715 | 1843184220 | 153559692 | 10100847
25 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.18425 | 1722602074 | 143513731 | 9440043
26 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.1722 | 1609908481 | 134124982 | 8822471
27 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.16093 | 1504587365 | 125350451 | 8245300
28 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.1504 | 1406156416 | 117149954 | 7705887
29 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.14056 | 1314164875 | 109485938 | 7201764
30 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.13137 | 1228191472 | 102323307 | 6730621
31 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.12277 | 1147842497 | 95629259 | 6290300
32 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.11474 | 1072749997 | 89373139 | 5878785
33 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.10723 | 1002570091 | 83526298 | 5494191
34 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.10022 | 936981393 | 78061961 | 5134758
35 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.093663 | 875683545 | 72955104 | 4798839
36 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.087535 | 818395837 | 68182340 | 4484897
37 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.081809 | 764855922 | 63721813 | 4191492
38 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.076457 | 714818619 | 59553096 | 3917282
39 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.071455 | 668054784 | 55657099 | 3661012
40 | 0 | 1000 | 0 | 200 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2606833463 | 599926945 | 9349306724 | 778911108 | 0.06678 | 624350265 | 52015981 | 3421506
41 | 0 | 1000 | 100 | 300 | 51235200 | 0 | 0 | 6742473262 | 553197047 | 0 | 0 | 0 | 0 | 0 | 0 | 2763953614 | 602812618 | 9506426875 | 781263573 | 0.062412 | 593311036 | 48759887 | 3197669
42 | 0 | 900 | 100 | 200 | 46111680 | 0 | 0 | 6068225936 | 497877342 | 0 | 0 | 0 | 0 | 0 | 0 | 2572256741 | 599466944 | 8640482677 | 744156842 | 0.058329 | 503987008 | 43405605 | 2689628
43 | 0 | 800 | 100 | 200 | 40988160 | 0 | 0 | 5393978609 | 442557638 | 0 | 0 | 0 | 0 | 0 | 0 | 2537635328 | 599043420 | 7931613938 | 712063690 | 0.054513 | 432373558 | 38816502 | 2234375
44 | 0 | 700 | 100 | 200 | 35864640 | 0 | 0 | 4719731283 | 387237933 | 0 | 0 | 0 | 0 | 0 | 0 | 2502963028 | 598656112 | 7222694311 | 683006904 | 0.050946 | 367970511 | 34796765 | 1827175
45 | 0 | 600 | 100 | 200 | 30741120 | 0 | 0 | 4045483957 | 331918228 | 0 | 0 | 0 | 0 | 0 | 0 | 2474257755 | 598523180 | 6519741712 | 657631979 | 0.047613 | 310427649 | 31312153 | 1463692
46 | 0 | 500 | 100 | 200 | 25617600 | 0 | 0 | 3371236631 | 276598523 | 0 | 0 | 0 | 0 | 0 | 0 | 2439456540 | 598202130 | 5810693171 | 635865292 | 0.044499 | 258567639 | 28295107 | 1139947
47 | 0 | 400 | 100 | 100 | 20494080 | 0 | 0 | 2696989305 | 221278819 | 0 | 0 | 0 | 0 | 0 | 0 | 2243435569 | 595048486 | 4940424874 | 615550645 | 0.041587 | 205459747 | 25599191 | 852297
48 | 0 | 300 | 100 | 100 | 15370560 | 0 | 0 | 2022741979 | 165959114 | 0 | 0 | 0 | 0 | 0 | 0 | 2214464763 | 595003435 | 4237206741 | 602853320 | 0.038867 | 164686624 | 23430973 | 597404
49 | 0 | 200 | 100 | 100 | 10247040 | 0 | 0 | 1348494652 | 110639409 | 0 | 0 | 0 | 0 | 0 | 0 | 2179315611 | 594781278 | 3527810263 | 594870811 | 0.036324 | 128144542 | 21608148 | 372215
50 | 0 | 100 | 100 | 100 | 5123520 | 0 | 0 | 674247326 | 55319705 | 0 | 0 | 0 | 0 | 0 | 0 | 2143921058 | 594585843 | 2818168385 | 592033001 | 0.033948 | 95670502 | 20098194 | 173932

## Parameters
Group | Parameter | Value | Units | Description | Source
--- SETTINGS ---
Settings | cross_sections_xml_location | /projects/MRP_MOUSE/openmc_data/endfb-viii.0-hdf5/cross_sections.xml |  | File path to the OpenMC cross sections XML file on HPC | User Input
Settings | plotting | Y |  | Whether to generate and save geometry plots (Y = yes, N = no) | User Input
Settings | simplified_chain_thermal_xml | /projects/MRP_MOUSE/openmc_data/simplified_thermal_chain11.xml |  | File path to the simplified depletion chain XML file for thermal reactors | User Input
--- MATERIALS ---
Materials | Axial Reflector | Graphite |  | Axial reflector material type — may differ from radial reflector | User Input
Materials | Common Temperature | 850 | K | Uniform operating temperature applied to all materials in isothermal simulations | User Input
Materials | Control Drum Absorber | B4C_enriched |  | Neutron absorber material in the control drums (e.g. B4C_enriched, B4C_natural) | User Input
Materials | Control Drum Reflector | Graphite |  | Reflector material in the control drums (e.g. Graphite) | User Input
Materials | Coolant | Helium |  | Primary coolant material type (e.g. NaK, Helium) | User Input
Materials | Enrichment | 0.15 | fraction | Uranium-235 enrichment fraction (0 to 1) | User Input
Materials | Fuel | UCO |  | Primary fuel material type (e.g. TRIGA_fuel, UO2, UN, UC, homog_TRISO) | User Input
Materials | Graphite Linear Expansion Coefficient | 4.3e-06 | 1/K | Mean linear thermal-expansion coefficient used to adjust GCMR graphite number density in density-aware temperature-coefficient cases. | User Input; IG-110 proxy from ORNL/TM-2017/705, Table 2.2, page 3
Materials | HX Material | SS316 |  | Heat exchanger structural material (e.g. SS316) | User Input
Materials | Matrix Material | Graphite |  | Background matrix material surrounding TRISO particles in the fuel compact | User Input
Materials | Moderator | Graphite |  | Neutron moderator material type (e.g. ZrH, Graphite, monolith_graphite) | User Input
Materials | Moderator Booster Materials | ['ZrH'] |  | List of moderator booster material names, from innermost to outermost region (e.g. ['ZrH'] or ['ZrH', 'Graphite']) | User Input
Materials | Radial Reflector | Graphite |  | Radial reflector material type (e.g. Graphite, BeO) | User Input
Materials | Shutdown Rod Absorber | B4C_enriched |  | Neutron absorber material used in the movable shutdown rods | User Input
Materials | Shutdown Rod Cladding | SS304 |  | Cladding material that moves with each shutdown-rod absorber | User Input
Materials | TRISO Fueled | Yes |  | Whether the reactor uses TRISO fuel particles (Yes or No) | User Input
Materials | UO2 atom fraction | 0.7 | fraction | Atom fraction of UO2 in the UCO mixed fuel (remainder is UC) | User Input
Materials | reactor type | GCMR |  | Reactor type identifier: LTMR (liquid metal thermal), GCMR (gas-cooled), or HPMR (heat pipe) | User Input
--- GEOMETRY ---
Geometry | Active Height | 200 | cm | Axial height of the active fuel region | User Input
Geometry | Assembly FTF | 19.4856 | cm | Assembly flat-to-flat distance (distance between opposite parallel faces of the hexagonal assembly). | User Input or Calculated
Geometry | Assembly Rings | 6 |  | Number of hexagonal lattice rings in one fuel assembly (GCMR) | User Input
Geometry | Axial Reflector Thickness | 9.7428 | cm | Thickness of each axial neutron reflector (top and bottom) | User Input
Geometry | Central Shutdown Rod Clad Radius | 1.05 | cm | Outer SS304 cladding radius for each shutdown rod in the central GCMR assembly. | User Input
Geometry | Central Shutdown Rod Count | 12 | rods | Number of shutdown rods in the central GCMR assembly. | User Input
Geometry | Central Shutdown Rod Radius | 0.85 | cm | B4C absorber radius for each shutdown rod in the central GCMR assembly. | User Input
Geometry | Central Shutdown Rod Ring | 2 |  | Hexagonal pin-lattice ring containing the central-assembly shutdown rods. | User Input
Geometry | Compact Fuel Radius | 0.6225 | cm | Radius of the cylindrical fuel compact region containing TRISO particles | User Input
Geometry | Coolant Channel Radius | 0.35 | cm | Radius of the coolant channels in the GCMR assembly | User Input
Geometry | Core Radius | 107.1706 | cm | Total core radius including the radial reflector | User Input or Calculated
Geometry | Core Rings | 5 |  | Number of assembly rings along the side of the hexagonal core (GCMR) | User Input
Geometry | Fuel Pin Materials | ['UCO', 'buffer_graphite', 'PyC', 'SiC', 'PyC'] |  | Ordered list of materials for each fuel pin region from innermost to outermost | User Input
Geometry | Fuel Pin Radii | [0.025, 0.035, 0.039, 0.0425, 0.0465] | cm | Ordered list of radii defining fuel pin region boundaries from innermost to outermost | User Input
Geometry | Lattice Pitch | 2.25 | cm | Center-to-center distance between adjacent lattice positions | User Input
Geometry | Moderator Booster Radii | [0.5] | cm | List of cumulative outer radii for moderator booster pin regions, innermost first (e.g. [0.55] or [0.40, 0.55]) | User Input
Geometry | Number of Shutdown Rods | 24 |  | Total shutdown-rod count. LTMR accepts user-selected 6- or 12-rod predefined layouts; GCMR calculates the total from the central and surrounding assembly inputs. | User Input or Calculated
Geometry | Packing Fraction | 0.4 | fraction | Volume fraction of TRISO particles within the fuel compact | User Input
Geometry | Radial Reflector Thickness | 9.7428 | cm | Thickness of the radial neutron reflector surrounding the active core | User Input
Geometry | Shutdown Rod Height | 200 | cm | Physical height of each LTMR shutdown rod; defaults to the active core height in the example input | User Input
Geometry | Surrounding Shutdown Assembly Count | 6 | assemblies | Number of first-ring GCMR assemblies containing the smaller surrounding shutdown rods. | User Input
Geometry | Surrounding Shutdown Rod Clad Radius | 0.65 | cm | Outer SS304 cladding radius for each shutdown rod in a surrounding GCMR shutdown assembly. | User Input
Geometry | Surrounding Shutdown Rod Count | 2 | rods per assembly | Number of shutdown rods in each surrounding GCMR shutdown assembly. | User Input
Geometry | Surrounding Shutdown Rod Radius | 0.45 | cm | B4C absorber radius for each shutdown rod in a surrounding GCMR shutdown assembly. | User Input
Geometry | Surrounding Shutdown Rod Ring | 2 |  | Hexagonal pin-lattice ring containing shutdown rods in each surrounding shutdown assembly. | User Input
Geometry | TRISO Packing Seed | 1 |  | Deterministic random seed used by OpenMC when packing TRISO particles in the representative fuel compact. | User Input
--- CONTROL DRUMS ---
Control Drums | All Drum Tubes Area | 7156.9408 | cm² | Total cross-sectional area removed from the reflector by all control-drum tubes, including clearance around each physical drum | Calculated
Control Drums | All Drums Area | 6849.1517 | cm² | Total cross-sectional area of all control drums | Calculated
Control Drums | All Drums Volume | 1503289.9809 | cm³ | Total volume of all control drums combined | Calculated
Control Drums | Control Drum Absorber Mass | 251.0797 | kg | Total mass of absorber material in all control drums | Calculated
Control Drums | Control Drum Reflector Mass | 2245.8483 | kg | Total mass of reflector material in all control drums | Calculated
Control Drums | Control Drums Mass | 2496.928 | kg | Total combined mass of all control drums (absorber + reflector) | Calculated
Control Drums | Drum Absorber Arc Degrees | 120 | degrees | Angular span of the absorber arc on each control drum; used by both OpenMC geometry and material inventory calculations | User Input
Control Drums | Drum Absorber Thickness | 1 | cm | Thickness of the absorber arc section within each control drum | User Input
Control Drums | Drum Count | 24 |  | Total number of control drums in the core; explicit and validated against the GCMR lattice. | User Input or Calculated
Control Drums | Drum Height | 219.4856 | cm | Height of the control drums (typically active height + 2x axial reflector thickness) | User Input
Control Drums | Drum Radius | 9.531 | cm | Outer radius of each control drum. If not specified, it is automatically set to the largest allowable value that avoids drum overlap. | User Input
Control Drums | Drum Tube Radius | 9.7428 | cm | Outer radius of the control drum tube. It is explicit and validated for the GCMR example and may be calculated for other models. | User Input or Calculated
--- CORE DESIGN ---
Core Design | Axial Reflector Mass | 901.8225 | kg | Total mass of both axial reflectors (top and bottom combined) | Calculated
Core Design | Axial Reflector Volume | 563639.0381 | cm³ | Combined volume of both LTMR axial reflectors, excluding control-drum tubes | Calculated
Core Design | GCMR Fuel Compact Count | 3697 | compacts | Number of GCMR fuel-compact positions remaining after shutdown-rod channels replace fuel positions | Calculated
Core Design | Moderator Booster Mass | 1351.1362 | kg | Total mass of moderator booster material in the core (GCMR) | Calculated
Core Design | Moderator Mass | 4076.7194 | kg | Total mass of the neutron moderator material in the core | Calculated
Core Design | Moderator Total Area | 12739.7482 | cm² | Total cross-sectional area occupied by moderator material in the core | Calculated
Core Design | Number Of TRISO Particles Per Compact Fuel | 231244 |  | Number of TRISO particles per fuel compact element | Calculated
Core Design | Radial Reflector Mass | 2837.7628 | kg | Total mass of the radial neutron reflector | Calculated
Core Design | Radial Reflector Volume | 1773601.7341 | cm³ | LTMR radial reflector volume over the active core height, excluding the hexagonal core and control-drum tubes | Calculated
Core Design | Shutdown Rod Absorber Mass | 17.5753 | kg | Total B4C absorber mass in all shutdown rods | Calculated
Core Design | Shutdown Rod Absorber Volume | 6974.3357 | cm³ | Total B4C absorber volume in all shutdown rods | Calculated
Core Design | Shutdown Rod Cladding Mass | 36.1007 | kg | Total cladding mass in all shutdown rods | Calculated
Core Design | Shutdown Rod Cladding Volume | 4523.8934 | cm³ | Total cladding volume in all shutdown rods | Calculated
Core Design | Shutdown Rods Mass | 53.676 | kg | Combined absorber and cladding mass of all shutdown rods | Calculated
Core Design | Total Number of TRISO Particles | 854909068 |  | Total number of TRISO particles in the entire core | Calculated
--- OVERALL SYSTEM ---
Overall System | Burnup Steps | [0.1, 0.2, 0.5, 1.0, 2.0, 5.0, 10.0, 15.0, 20.0, 30.0, 40.0, 50.0, 60.0, 80.0, 100.0, 120.0] | MWd/kg | Cumulative burnup values at each depletion time step | User Input
Overall System | Heat Flux | 0.02234 | MW/m² | Calculated average fuel surface heat flux at full power | Calculated
Overall System | Heat Flux Criteria | 0.9 | MW/m² | Maximum allowable fuel surface heat flux (design constraint) | User Input
Overall System | Power MWe | 6 | MWe | Reactor net electric power output (thermal power × thermal efficiency) | Calculated
Overall System | Power MWt | 15 | MWt | Reactor thermal power output | User Input
Overall System | Thermal Efficiency | 0.4 | fraction | Net thermal-to-electric conversion efficiency of the power conversion system | User Input
--- PHYSICS RESULTS ---
Physics Results | Fuel Lifetime | 1786 | days | Estimated fuel cycle length — time for the 3D-corrected keff to fall to 1.0 | Calculated
Physics Results | Fuel Tail Waste Mass | 17703.5094 | kg | Mass of depleted uranium tails produced during the enrichment process | Calculated
Physics Results | Mass U235 | 85655.7587 | g | Initial mass of U-235 in the fresh fuel load | Calculated
Physics Results | Mass U238 | 484226.2802 | g | Initial mass of U-238 in the fresh fuel load | Calculated
Physics Results | Natural Uranium Mass | 18273.3915 | kg | Mass of natural uranium feed required to produce the enriched fuel | Calculated
Physics Results | SWU | 17213.4623 | kg-SWU | Separative work units required to produce the enriched fuel | Calculated
Physics Results | Uranium Mass | 569.882 | kg | Total initial uranium mass in the fresh fuel load (U-235 + U-238) | Calculated
--- PRIMARY LOOP & BALANCE OF PLANT ---
Primary Loop & Balance of Plant | BoP Count | 2 |  | Number of Balance of Plant (power conversion) systems | User Input
Primary Loop & Balance of Plant | BoP Power kWe | 3000 | kWe | Electric power handled by each BoP system | Calculated
Primary Loop & Balance of Plant | BoP per loop load fraction | 0.5 | fraction | Fraction of total electric load handled by each BoP system | User Input
Primary Loop & Balance of Plant | Compressor Isentropic Efficiency | 0.8 | fraction | Isentropic efficiency of the gas compressor (GCMR) | User Input
Primary Loop & Balance of Plant | Compressor Pressure Ratio | 4 |  | Compressor pressure ratio for gas-cooled reactor (GCMR) | User Input
Primary Loop & Balance of Plant | Coolant Mass Flow Rate | 11.554 | kg/s | Total primary coolant mass flow rate | Calculated
Primary Loop & Balance of Plant | Integrated Heat Transfer Vessel Material | SA508 |  | Material of the integrated heat transfer vessel (GCMR) | User Input
Primary Loop & Balance of Plant | Integrated Heat Transfer Vessel Thickness | 0 | cm | Wall thickness of the integrated heat transfer vessel (GCMR, 0 if none) | User Input
Primary Loop & Balance of Plant | Primary HX Mass | 1507.4142 | kg | Calculated mass of the primary heat exchanger | Calculated
Primary Loop & Balance of Plant | Primary Loop Compressor Power | 108437.0872 | W | Mechanical power required to drive the primary loop gas compressor (GCMR) | Calculated
Primary Loop & Balance of Plant | Primary Loop Count | 2 |  | Number of primary coolant loops | User Input
Primary Loop & Balance of Plant | Primary Loop Inlet Temperature | 573.15 | K | Primary coolant temperature at the core inlet | User Input
Primary Loop & Balance of Plant | Primary Loop Mass Flow Rate | 5.777 | kg/s | Coolant mass flow rate per primary loop | Calculated
Primary Loop & Balance of Plant | Primary Loop Outlet Temperature | 823.15 | K | Primary coolant temperature at the core outlet | User Input
Primary Loop & Balance of Plant | Primary Loop Pressure Drop | 50000 | Pa | Pressure drop across the primary coolant loop | User Input
Primary Loop & Balance of Plant | Primary Loop Purification | FALSE |  | Whether primary coolant purification is used (reduces coolant replacement frequency) | User Input
Primary Loop & Balance of Plant | Primary Loop per loop load fraction | 0.5 | fraction | Fraction of total thermal load handled by each primary coolant loop | User Input
Primary Loop & Balance of Plant | Secondary HX Mass | 0 | kg | Mass of the secondary heat exchanger (0 if none) | User Input
Primary Loop & Balance of Plant | Secondary Loop Inlet Temperature | 543.15 | K | Secondary loop coolant temperature at the heat exchanger inlet | User Input
Primary Loop & Balance of Plant | Secondary Loop Outlet Temperature | 773.15 | K | Secondary loop coolant temperature at the heat exchanger outlet | User Input
--- SHIELDING ---
Shielding | In Vessel Shield Inner Radius | 107.1706 | cm | Inner radius of the in-vessel radiation shield (equal to core radius) | User Input
Shielding | In Vessel Shield Mass | 0 | kg | Total mass of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Material | B4C_natural |  | Material of the in-vessel radiation shield | User Input
Shielding | In Vessel Shield Outer Radius | 107.1706 | cm | Outer radius of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Thickness | 0 | cm | Thickness of the in-vessel radiation shield (0 if none) | User Input
Shielding | Out Of Vessel Shield Effective Density Factor | 0.5 | fraction | Effective density factor for the out-of-vessel shield — accounts for partial fill (e.g. 0.5 = 50% fill) | User Input
Shielding | Out Of Vessel Shield Mass | 6532.5405 | kg | Total mass of the out-of-vessel radiation shield | Calculated
Shielding | Out Of Vessel Shield Material | WEP |  | Material of the out-of-vessel radiation shield | User Input
Shielding | Out Of Vessel Shield Thickness | 39.37 | cm | Thickness of the out-of-vessel radiation shield | User Input
Shielding | Outer Shield Inner Radius | 120.6706 | cm | Inner radius of the out-of-vessel shield | Calculated
Shielding | Outer Shield Outer Radius | 160.0406 | cm | Outer radius of the out-of-vessel shield (outermost boundary of the shielded assembly) | Calculated
--- VESSELS ---
Vessels | Cooling Vessel Mass | 1064.7695 | kg | Total mass of the cooling vessel | Calculated
Vessels | Cooling Vessel Material | stainless_steel |  | Structural material of the cooling vessel | User Input
Vessels | Cooling Vessel Radius | 115.1706 | cm | Outer radius of the cooling vessel | Calculated
Vessels | Cooling Vessel Thickness | 0.5 | cm | Wall thickness of the cooling vessel | User Input
Vessels | Gap Between Cooling Vessel And Intake Vessel | 5 | cm | Radial gap between the cooling vessel and intake vessel | User Input
Vessels | Gap Between Guard Vessel And Cooling Vessel | 5 | cm | Radial gap between the guard vessel and cooling vessel | User Input
Vessels | Gap Between Vessel And Guard Vessel | 0 | cm | Radial gap between the reactor vessel and guard vessel | User Input
Vessels | Guard Vessel Mass | 0 | kg | Total mass of the guard vessel | Calculated
Vessels | Guard Vessel Material | low_alloy_steel |  | Structural material of the guard vessel | User Input
Vessels | Guard Vessel Radius | 110.1706 | cm | Outer radius of the guard vessel | Calculated
Vessels | Guard Vessel Thickness | 0 | cm | Wall thickness of the guard vessel (0 if none) | User Input
Vessels | Intake Vessel Mass | 1125.6629 | kg | Total mass of the intake vessel | Calculated
Vessels | Intake Vessel Material | stainless_steel |  | Structural material of the intake vessel | User Input
Vessels | Intake Vessel Radius | 120.1706 | cm | Outer radius of the intake vessel | Calculated
Vessels | Intake Vessel Thickness | 0.5 | cm | Wall thickness of the intake vessel | User Input
Vessels | Integrated Heat Transfer Vessel Mass | 0 | kg | Total mass of the integrated heat transfer vessel (GCMR, 0 if none) | Calculated
Vessels | Integrated Heat Transfer Vessel Outer Volume | 0 | cm³ | Outer volume of the integrated heat transfer vessel (GCMR, 0 if none) | Calculated
Vessels | RPV Outer Height | 366.8956 | cm | Total outer height of the reactor pressure vessel including heads | Calculated
Vessels | RPV Outer Radius | 110.1706 | cm | Outer radius of the reactor pressure vessel (inner radius + wall thickness) | Calculated
Vessels | Total Vessels Mass | 9096.5456 | kg | Combined mass of all vessel components (pressure vessel, guard, cooling, intake) | Calculated
Vessels | Vessel Bottom Depth | 32.129 | cm | Depth of the vessel bottom head (ellipsoidal) | User Input
Vessels | Vessel Height | 296.6376 | cm | Total height of the reactor pressure vessel | Calculated
Vessels | Vessel Lower Plenum Height | 30 | cm | Height of the lower plenum region below the active core | User Input
Vessels | Vessel Mass | 6906.1132 | kg | Total mass of the reactor pressure vessel | Calculated
Vessels | Vessel Material | stainless_steel |  | Structural material of the reactor pressure vessel | User Input
Vessels | Vessel Radius | 107.1706 | cm | Inner radius of the reactor pressure vessel (or core barrel) | User Input
Vessels | Vessel Thickness | 3 | cm | Wall thickness of the reactor pressure vessel | User Input
Vessels | Vessel Upper Gas Gap | 0 | cm | Height of the upper gas gap above the upper plenum (0 if none) | User Input
Vessels | Vessel Upper Plenum Height | 47.152 | cm | Height of the upper plenum region above the active core | User Input
Vessels | Vessels Total Height | 342.2666 | cm | Total height of the complete vessel assembly | Calculated
Vessels | Vessels Total Radius | 120.6706 | cm | Total outer radius of the complete vessel assembly | Calculated
--- OPERATION ---
Operation | A75: Inner Vessel Structure Replacement Period (cycles) | 2 | cycles | Number of fuel cycles between scheduled inner vessel structure replacements | User Input
Operation | A75: Moderator Booster Replacement Period (cycles) | 1 | cycles | Number of complete fuel cycles between moderator booster replacements | User Input
Operation | A75: Moderator Replacement Period (cycles) | 1 | cycles | Number of complete fuel cycles between moderator replacements | User Input
Operation | A75: Outer Vessel Structure Replacement Period (years) | 20 | years | Service period in years between scheduled outer vessel structure replacements | User Input
Operation | A75: Reactor Control Devices Replacement Period (cycles) | 2 | cycles | Number of fuel cycles between scheduled reactor control device replacements | User Input
Operation | A75: Reflector Replacement Period (cycles) | 2 | cycles | Number of fuel cycles between scheduled reflector replacements | User Input
Operation | A78: CAPEX to Decommissioning Cost Ratio | 0.15 | fraction | Ratio of total decommissioning cost to total capital cost (typical range: 9%–15%) | User Input
Operation | Annual Coolant Supply Frequency | 4 | deliveries/year | Number of coolant resupply deliveries per year (1 if purified, 6 if not) | Calculated
Operation | Annual Electricity Production | 51235.2 | MWh/year | Total annual electricity production at the calculated capacity factor | Calculated
Operation | Capacity Factor | 0.97479 | fraction | Annual plant capacity factor — fraction of the year the plant operates at full power | Calculated
Operation | Emergency Shutdowns Per Year | 0.2 | events/year | Expected number of unplanned emergency shutdowns per year | User Input
Operation | Levelization Period | 40 | years | Plant lifetime used for LCOE levelization (economic analysis period) | User Input
Operation | Maintenance to Direct Cost Ratio | 0.03 | fraction | Ratio of annual non-replacement maintenance cost to total direct capital cost | User Input
Operation | Number of On-Site Operators per Shift | 2 |  | Number of concurrent on-site operators assigned per shift | User Input
Operation | Onsite Coolant Inventory | 49.5 | kg | Total mass of coolant stored on site (fresh + used tanks) | User Input
Operation | Operation Mode | On-Site Staffed and Remotely Monitored |  | Reactor operation mode: Remotely Monitored, On-Site Staffed, or On-Site Staffed and Remotely Monitored | User Input
Operation | Reactors Monitored Per Operator | 9 |  | Number of reactors that can be monitored by a single operator | User Input
Operation | Refueling Period | 30 | days | Duration of the scheduled refueling outage | User Input
Operation | Replacement Coolant Inventory | 4.95 | kg | Mass of coolant replaced per refueling cycle | User Input
Operation | Security Staff Per Shift | 1 |  | Number of security personnel required per shift | User Input
Operation | Startup Duration after Emergency Shutdown | 14 | days | Duration of the startup sequence following an emergency shutdown | User Input
Operation | Startup Duration after Refueling | 2 | days | Duration of the startup sequence following a refueling outage | User Input
--- ECONOMIC PARAMETERS ---
Economic Parameters | Annual Return | 0.0475 | fraction | Annual return rate assumed for the decommissioning reserve fund | User Input
Economic Parameters | Assumed Number Of Units For Onsite Learning | 200 |  | Number of units assumed for onsite learning (typically 2 × NOAK Unit Number) | Calculated
Economic Parameters | Construction Duration | 12 | months | Duration of plant construction used for financing cost calculation | User Input
Economic Parameters | Control Building Basement Volume | 5.9448 | m³ | Volume of concrete in the control building basement | User Input
Economic Parameters | Control Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the control building exterior walls | User Input
Economic Parameters | Control Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the control building slab roof | User Input
Economic Parameters | Debt To Equity Ratio | 1 | fraction | Ratio of debt financing to equity financing for the project | User Input
Economic Parameters | Discount Rate | 0.07 | fraction | Annual discount rate (WACC) used for LCOE levelization and cost annualization | User Input
Economic Parameters | Emergency Building Basement Volume | 0 | m³ | Volume of concrete in the emergency building basement (0 if none) | User Input
Economic Parameters | Emergency Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the emergency building exterior walls (0 if none) | User Input
Economic Parameters | Emergency Building Slab Roof Volume | 0 | m³ | Volume of concrete in the emergency building slab roof (0 if none) | User Input
Economic Parameters | Escalation Year | 2025 | year | Reference year to which all costs are escalated for consistent comparison | User Input
Economic Parameters | Excavation Volume | 412.605 | m³ | Volume of earth to be excavated for plant construction | User Input
Economic Parameters | FTEs Per Offsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per offsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per onsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator Per Year | 5 | FTE/operator/year | Total FTE-years per operator per year including all activities | Calculated
Economic Parameters | FTEs Per Operator Per Year Per Refueling | 0.033333 | FTE/operator/year | Fraction of an FTE spent per operator per year on refueling-related activities | User Input
Economic Parameters | FTEs Per Security Staff (24/7) | 5 | FTE/staff | Full-time equivalents needed per security staff position to maintain 24/7 coverage | User Input
Economic Parameters | Hours Per FTE | 1800 | hours/year | Annual working hours per full-time equivalent employee | User Input
Economic Parameters | Integrated Heat Exchanger Building Basement Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building basement (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building exterior walls (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Slab Roof Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building slab roof (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Superstructure Area | 0 | m² | Floor area of the integrated heat exchanger building superstructure (0 if none) | User Input
Economic Parameters | Interest Rate | 0.07 | fraction | Annual cost of debt used to calculate interest during construction (Account 62) | User Input
Economic Parameters | Land Area | 18 | acres | Total land area required for the plant site | User Input
Economic Parameters | Manipulator Building Basement Volume | 17.8374 | m³ | Volume of concrete in the manipulator building basement | User Input
Economic Parameters | Manipulator Building Exterior Walls Volume | 15.9195 | m³ | Volume of concrete in the manipulator building exterior walls | User Input
Economic Parameters | Manipulator Building Slab Roof Volume | 4.7566 | m³ | Volume of concrete in the manipulator building slab roof | User Input
Economic Parameters | NOAK Unit Number | 100 |  | Nth-of-a-kind unit number used to calculate the learning curve cost multiplier | User Input
Economic Parameters | Number of Samples | 100 |  | Number of Monte Carlo samples used for cost uncertainty quantification | User Input
Economic Parameters | Radwaste Building Basement Volume | 0 | m³ | Volume of concrete in the radioactive waste building basement (0 if none) | User Input
Economic Parameters | Radwaste Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the radioactive waste building exterior walls (0 if none) | User Input
Economic Parameters | Radwaste Building Slab Roof Volume | 0 | m³ | Volume of concrete in the radioactive waste building slab roof (0 if none) | User Input
Economic Parameters | Reactor Building Basement Volume | 95.0976 | m³ | Volume of concrete in the reactor building basement | User Input
Economic Parameters | Reactor Building Exterior Walls Volume | 129.9564 | m³ | Volume of concrete in the reactor building exterior walls | User Input
Economic Parameters | Reactor Building Slab Roof Volume | 95.0976 | m³ | Volume of concrete in the reactor building slab roof | User Input
Economic Parameters | Reactor Building Superstructure Area | 77 | m² | Floor area of the reactor building superstructure | User Input
Economic Parameters | Refueling Building Basement Volume | 0 | m³ | Volume of concrete in the refueling building basement (0 if none) | User Input
Economic Parameters | Refueling Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the refueling building exterior walls (0 if none) | User Input
Economic Parameters | Refueling Building Slab Roof Volume | 0 | m³ | Volume of concrete in the refueling building slab roof (0 if none) | User Input
Economic Parameters | Spent Fuel Building Basement Volume | 0 | m³ | Volume of concrete in the spent fuel building basement (0 if none) | User Input
Economic Parameters | Spent Fuel Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the spent fuel building exterior walls (0 if none) | User Input
Economic Parameters | Spent Fuel Building Slab Roof Volume | 0 | m³ | Volume of concrete in the spent fuel building slab roof (0 if none) | User Input
Economic Parameters | Storage Building Basement Volume | 11.76 | m³ | Volume of concrete in the storage building basement | User Input
Economic Parameters | Storage Building Exterior Walls Volume | 15.768 | m³ | Volume of concrete in the storage building exterior walls | User Input
Economic Parameters | Storage Building Slab Roof Volume | 11.76 | m³ | Volume of concrete in the storage building slab roof (houses operational spares) | User Input
Economic Parameters | Turbine Building Basement Volume | 5.9448 | m³ | Volume of concrete in the turbine building basement | User Input
Economic Parameters | Turbine Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the turbine building exterior walls | User Input
Economic Parameters | Turbine Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the turbine building slab roof | User Input
Economic Parameters | Work Hours Per Shift | 10 | hours | Duration of each work shift | User Input
Economic Parameters | indirect to direct field-related cost | 0.06539 | fraction | Ratio of indirect field (site) costs to total direct field costs — covers site supervision, temporary facilities, and other indirect site activities | User Input
--- CENTRAL FACILITY ---
Central Facility | Annual Reactor Cask Replacement | 5 | casks/year | Annual replacement rate for reactor transport casks. | User Input
Central Facility | Max Reactors Per Servicing Facility | 1000 | reactors/facility | Maximum number of reactors assigned to one servicing facility. | User Input
Central Facility | Reactor Transport Vehicle Count | 10 |  | Number of vehicles for transporting reactor units to/from field sites. | User Input
Central Facility | SER Operator FTEs Per Facility | 248 | FTE/facility | Total annual operator FTE headcount for one servicing facility; used directly to calculate servicing-campus Account 711. | Calculated
Central Facility | Servicing Facility Count | 1 | facilities | Number of servicing facilities required for the fleet. | Calculated
Central Facility | Servicing Facility Design Capacity | 1000 | reactors/facility | Standard facility capacity based on the largest assigned reactor count. | Calculated
Central Facility | Servicing Facility Reactor Counts | (1000,) | reactors | Balanced whole-reactor allocation across servicing facilities. | Calculated
Central Facility | Servicing Hot Cell Count | 2 |  | Number of hot cells for reactor servicing operations. | User Input
Central Facility | Servicing Rate Per Facility | 200.9912 | reactors/year/facility | Fleet servicing rate distributed evenly across facilities. | Calculated
--- LEARNING RATES ---
Learning Rates | Cask Learning Cap | 100 | casks | Cask number after which unit-cost learning stops. | User Input
Learning Rates | Cask Learning Rate | 0.15 | fraction per doubling | Unit-cost reduction for each doubling of cask production experience. | User Input
Learning Rates | Factory Be | 0.41505 | fraction | Learning rate for factory-manufactured beryllium components | User Input
Learning Rates | Factory Be Cost Multiplier | 0.028363 | fraction | NOAK cost multiplier for beryllium components based on Wright's Law | Calculated
Learning Rates | Factory BeO | 0.39915 | fraction | Learning rate for factory-manufactured beryllium oxide components | User Input
Learning Rates | Factory BeO Cost Multiplier | 0.033897 | fraction | NOAK cost multiplier for beryllium oxide components based on Wright's Law | Calculated
Learning Rates | Factory Drums | 0.24138 | fraction | Learning rate for factory-manufactured control drum components | User Input
Learning Rates | Factory Drums Cost Multiplier | 0.15955 | fraction | NOAK cost multiplier for factory-built control drums based on Wright's Law | Calculated
Learning Rates | Factory Other | 0.22963 | fraction | Learning rate for other factory-manufactured components | User Input
Learning Rates | Factory Other Cost Multiplier | 0.17671 | fraction | NOAK cost multiplier for other factory-built components based on Wright's Law | Calculated
Learning Rates | Factory Primary Structure | 0.18443 | fraction | Learning rate for factory-manufactured primary structural components | User Input
Learning Rates | Factory Primary Structure Cost Multiplier | 0.25808 | fraction | NOAK cost multiplier for factory-built primary structure based on Wright's Law | Calculated
Learning Rates | Licensing Learning | 0.2 | fraction | Learning rate for licensing costs per doubling of cumulative units produced | User Input
Learning Rates | Licensing Learning Cost Multiplier | 0.22706 | fraction | NOAK cost multiplier for licensing costs based on Wright's Law | Calculated
Learning Rates | No Learning | 0 | fraction | Learning rate for components with no learning benefit (fixed costs, rate = 0) | User Input
Learning Rates | No Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for components with no learning (always 1.0) | Calculated
Learning Rates | Non-nuclear off-the-shelf | 0.05 | fraction | Learning rate for non-nuclear commercial off-the-shelf components | User Input
Learning Rates | Non-nuclear off-the-shelf Cost Multiplier | 0.71121 | fraction | NOAK cost multiplier for non-nuclear commercial components based on Wright's Law | Calculated
Learning Rates | Onsite Learning | 0.08 | fraction | Learning rate for onsite construction and installation activities | User Input
Learning Rates | Onsite Learning Cost Multiplier | 0.57466 | fraction | NOAK cost multiplier for onsite construction activities based on Wright's Law | Calculated
Learning Rates | Servicing Facility Learning Cap | 5 | facilities | Facility number after which servicing-facility OCC learning stops. | User Input
Learning Rates | Servicing Facility OCC Learning Multipliers | (1.0,) | fraction | Sequential OCC multiplier for each servicing facility. | Calculated
Learning Rates | Servicing Facility OCC Learning Rate | 0.3 | fraction per doubling | OCC reduction for each doubling of servicing-facility experience. | User Input
--- UNCATEGORIZED ---
Uncategorized | Annual Radwaste Cask Consumption | 100.4956 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Annual Used Fuel Cask Consumption | 200.9912 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Average Distance From Serv to GenSite | 1000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | CoolantInventoryRPV_Mass | 40.5125 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Cycle Length | 4.9753 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Deployment Period | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dwell Time GenSite | 0.0027397 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dwell Time Reactor Transport GenSite | 0.0054795 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dwell Time Reactor Transport Serv | 0.0054795 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dwell Time Serv | 0.0027397 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Extra RPV Fraction | 0.015 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Fleet | 1000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Fleet Mode | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Fuel Mass In Core | 569.882 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | GenSite Downtime | 0.083333 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Generating Sites Count | 973 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | He Gas Replenishment | 19354.4056 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | He Gas Replenishment Per Hot Cell | 3737.25 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Helicopter Count | 2 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Helium Purification and Storage Building Area | 975.2897 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Helium Transport Truck Count | 71 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 223 to Reactor OCC per Testing Line Ratio | 0.1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 30 to Account 20 Ratio | 0.5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 716 to Accounts 711-715 Ratio | 0.02 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 717 to Accounts 711-715 Ratio | 0.075 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 741 to Account 20 Ratio | 0.005 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 742 to Account 20 Ratio | 0.05 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 743 to Account 20 Ratio | 0.01 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 747.1 to Accounts 741-743 Ratio | 0.05 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Account 747.4 to Account 20 Ratio | 0.005 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Administration Building Area | 4644.8282 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Campus Land Area | 63.4995 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Campus Power | 1.4376 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Construction Duration | 36 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Emergency Generator Power | 4.9992 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Fire Station Count | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Guard Station Count | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Local Control Building Area | 80 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Local Transport Vehicle Count | 2 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Maintenance Staff Headcount | 6 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Motion Detector Count | 108 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Protected Perimeter | 1590.7705 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Road Length | 1828.8021 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Security Building Area | 815.244 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Security Camera Count | 68 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Security Staff Per Shift | 6 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Site Perimeter | 1828.8021 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Switchyard Rating | 3 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Testing Coolant Allotment | 153.8153 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Testing Engineering Headcount | 8 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Testing Line Annual Rate | 86 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Testing Line Count | 2 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Testing Number of Operators | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Utility Vehicle Count | 3 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Warehouse Building Area | 6499.9414 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | MFG Warehouse Staff | 7 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Maintenance Truck Count | 8 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Maintenance Visit Frequency | 0.40198 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Manufacturing Campus Area | 63.4995 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Moderator Booster Mass ZrH | 1351.1362 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Parts Service Center and Warehouse Building Area | 8487.5708 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Production Rate | 100 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Radioactive Waste Processing Hot Cell Count | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Radwaste Storage Warehouses Area | 1007593.8845 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Reactor Transport Cask Count | 100 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Roundtrip Time | 0.011416 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Roundtrip Time Reactor Transport | 0.030441 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 30 to Account 20 Ratio | 0.5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 716 to Accounts 711-715 Ratio | 0.02 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 717 to Accounts 711-715 Ratio | 0.075 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 741 to Account 20 Ratio | 0.005 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 742 to Account 20 Ratio | 0.05 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 743 to Account 20 Ratio | 0.01 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 747.1 to Accounts 741-743 Ratio | 0.05 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Account 747.4 to Account 20 Ratio | 0.005 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Administration Building Area | 23969.5673 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Campus Area | 540.1638 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Campus Land Area | 540.1638 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Construction Duration | 36 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Controlled Perimeter | 0 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Emergency Generator Power | 46.5784 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Engineering Headcount | 444 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Fire Station Count | 3 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Guard Station Count | 4 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Helium Flowrate | 0.00068145 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Local Control Building Area | 2680 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Local Transport Vehicle Count | 2 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Maintenance Staff Per Shift | 1983 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Motion Detector Count | 919 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Protected Perimeter | 1576.3052 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Rad Waste Management Building Area | 927.5406 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Radiation Monitor Count | 3 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Remote Control Building Area | 2680 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Road Length | 1775.79 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Security Building Area | 815.244 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Security Camera Count | 579 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Security Staff Per Shift | 37 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Site Perimeter | 1775.79 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Switchyard Average Power | 113.3764 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Switchyard Rating | 226.7528 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | SER Utility Vehicle Count | 37 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Service Air Water Building Count | 3 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Servicing Hot Cell Annual Rate | 111 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Servicing Hot Cell Building Area | 21600.1572 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Servicing Rate | 200.9912 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Servicing Total Time | 0.027397 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shift To Headcount | 5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Used Fuel Storage Lifetime Capacity | 5632719.5253 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Water Supply Frequency | 4 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Water Tanker Truck Count | 71 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | m3_to_kg_He_RT_atmospheric | 0.1661 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown