## Cost Database
Account | Level | Account Name | Account Title | Standard Cost Equation? | Optional Variable | Optional Value | Sec Optional Variable | Sec Optional Value | Fixed Cost ($) | Unit Cost | Unit Cost (units) | Scaling Variable | Scaling Variable Ref Value | Units | Exponent | Dollar Year | Type | Source | Ref | Link | Notes | FOAK to NOAK Multiplier Type | Fixed Cost Low End | Fixed Cost High End | Fixed Cost Distribution | Unit Cost Low End | Unit Cost High End | Unit Cost Distribution | Exponent std | Exponent Max | Exponent Min | Exponent Distribution
10 | 0 | Capitalized Pre-Construction Costs | Capitalized Pre-Construction Costs
11 | 1 | Land Cost | Land Cost | standard | [5 empty] | 3800 | $/acres | Land Area |  | acres |  | 2022 | General | The average cost per acre for rural land in 2022 from the US Department of Agriculture | Abou-Jaoude, A., Lohse, C. S., Larsen, L. M., Guaita, N., Trivedi, I., Joseck, F. C., ... & Stein, A. (2024). Meta-analysis of advanced nuclear reactor cost estimations (No. INL/RPT-24-77048-Rev001). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_107010.pdf |  | No Learning | 0 | 0 | Lognormal | 3420 | 4940 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
12 | 1 | Site Permits | Site Permits | standard | [5 empty] | 10030 | $/MWe | Power MWe |  | MWe |  | 2022 | Labor | Data from SMR MHTGRs |  |  |  | No Learning | 0 | 0 | Lognormal | 9027 | 13039 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
13 | 1 | Plant Licensing | Plant Licensing | standard |  |  |  |  | 28113008 | [6 empty] | 2025 | Labor | NRC Website | According to NRC, the number of hours range from 108K to 257K hours https://www.nrc.gov/docs/ML2301/ML23018A174.pdf For the hourly rate: 154$/hour https://www.federalregister.gov/documents/2026/06/16/2026-12067/fee-schedules-fee-recovery-for-fiscal-year-2026 | https://art.inl.gov/NGNP/INL%20Documents/Year%202012/Assessment%20of%20High%20Temperature%20Gas-Cooled%20Reactor%20-%20HTGR%20-%20Capital%20and%20Operating%20Costs.pdf |  | Licensing Learning | 16632000 | 39594016 | Uniform | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
14 | 1 | Plant Permits | Plant Permits | standard |  |  |  |  | 3000000 | [6 empty] | 2009 | Labor | NGNP project | Gandrik, A., B. Wallace, L. Demick, S. Melancon and M. Patterson (2011). "Assessment of high temperature gas-cooled reactor (HTGR) capital and operating costs." Idaho National Laboratory, TEV-1196, Idaho Falls, ID. |  |  | No Learning | 2700000 | 4500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
15 | 1 | Plant Studies | Plant Studies | standard |  |  |  |  | 5210451 | [6 empty] | 2024 | Labor | MARVEL Project (Labor-adjusted Cost) | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf | MARVEL's data were updated | No Learning | 4689405.9 | 7815676.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
20 | 0 | Capitalized Direct Costs | Capitalized Direct Costs
21 | 1 | Structures and Improvements | Structures and Improvements
211 | 2 | Site Preparation/ Yard Work | Site Preparation/ Yard Work
211.1 | 3 | Cleaning and Grubbing | Cleaning and Grubbing | standard | [5 empty] | 5862.8794 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 5276.5915 | 7621.7432 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.2 | 3 | Stripping Topsoil | Stripping Topsoil | standard | [5 empty] | 3411.716 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 3070.5444 | 4435.2308 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.3 | 3 | Excavation | Excavation | standard | [5 empty] | 32.004 | $/m^3 | Excavation Volume |  | m^3 |  | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 28.8036 | 41.6052 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.4 | 3 | Roads | Roads | standard | [5 empty] | 8867.5852 | $/m | GEN Road Length |  | m |  | 2025 | General | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 7980.8266 | 11527.8607 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.9 | 3 | Security Fencing | Security Fencing
211.91 | 4 | Security Fencing Limited | Security Fencing Limited | standard | [5 empty] | 627.8336 | $/m | Limited Perimeter |  | m |  | 2025 | General | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 565.0502 | 816.1836 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.93 | 4 | Security Fencing Protected | Security Fencing Protected | standard | [5 empty] | 34869.0609 | $/m | Protected Perimeter |  | m |  | 2025 | General | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 31382.1548 | 45329.7792 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212 | 2 | Reactor Island Civil Structures | Reactor Island Civil Structures
212.1 | 3 | Reactor Building Slab Roof | Reactor Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Reactor Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.2 | 3 | Reactor Building Basement | Reactor Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Reactor Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.3 | 3 | Reactor Building Walls | Reactor Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Reactor Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.4 | 3 | Reactor Building Liner | Reactor Building Liner | standard | [5 empty] | 6491.9267 | $/m^2 | Reactor Building Superstructure Area | 9373 | m^2 | 1 | 2018 | Lab and Mat and Equip | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | https://doi.org/10.1016/j.rser.2021.111880 |  | Onsite Learning | 0 | 0 | Lognormal | 5842.734 | 8439.5047 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
212.5 | 3 | Reactor Building HVAC | Reactor Building HVAC | standard | [5 empty] | 1731.9189 | $/MWt | Power MWt | 3417 | MWt | 0.8 | 2018 | Lab and Mat and Equip | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | https://doi.org/10.1016/j.rser.2021.111880 |  | Onsite Learning | 0 | 0 | Lognormal | 1558.727 | 2251.4946 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213 | 2 | Main Function Buildings | Main Function Buildings
213.1 | 3 | Energy conversion Building | Energy conversion Building
213.11 | 4 | Energy Conversion Building Slab Roof | Energy Conversion Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Turbine Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.12 | 4 | Energy Conversion Building Basement | Energy Conversion Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Turbine Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.13 | 4 | Energy Conversion Building Walls | Energy Conversion Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Turbine Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.2 | 3 | Control building | Control building
213.21 | 4 | Control Building Slab Roof | Control Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Control Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.22 | 4 | Control Building Basement | Control Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Control Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.23 | 4 | Control Building Walls | Control Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Control Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.3 | 3 | Integrated Heat Exchanger Building | Integrated Heat Exchanger Building |  | reactor type | GCMR
213.31 | 4 | Integrated Heat Exchanger Building Slab Roof | Integrated Heat Exchanger Building Slab Roof | standard | reactor type | GCMR |  |  |  | 1200 | $/m^3 | Integrated Heat Exchanger Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.32 | 4 | Integrated Heat Exchanger Building Basement | Integrated Heat Exchanger Building Basement | standard | reactor type | GCMR |  |  |  | 943.9 | $/m^3 | Integrated Heat Exchanger Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.33 | 4 | Integrated Heat Exchanger Building Walls | Integrated Heat Exchanger Building Walls | standard | reactor type | GCMR |  |  |  | 721.21 | $/m^3 | Integrated Heat Exchanger Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
213.34 | 4 | Integrated Heat Exchanger Building Liner | Integrated Heat Exchanger Building Liner | standard | reactor type | GCMR |  |  |  | 6491.9267 | $/m^2 | Integrated Heat Exchanger Building Superstructure Area | 9373 | m^2 | 1 | 2018 | Lab and Mat and Equip | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | Stewart W.R., Shirvan K., "Capital cost estimation for advanced nuclear power plants," Renewable and Sustainable Energy Reviews, Nov. 2021, 111880 | https://doi.org/10.1016/j.rser.2021.111880 |  | Onsite Learning | 0 | 0 | Lognormal | 5842.734 | 8439.5047 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214 | 2 | Buildings to Support Main Function | Buildings to Support Main Function
214.1 | 3 | Fuel Management Buildings | Fuel Management Buildings
214.11 | 4 | Refueling Building | Refueling Building
214.111 | 5 | Refueling Building Slab Roof | Refueling Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Refueling Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 |  | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.112 | 5 | Refueling Building Basement | Refueling Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Refueling Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.113 | 5 | Refueling Building Walls | Refueling Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Refueling Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.12 | 4 | Spent Fuel Building | Spent Fuel Building
214.121 | 5 | Spent Fuel Building Slab Roof | Spent Fuel Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Spent Fuel Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.122 | 5 | Spent Fuel Building Basement | Spent Fuel Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Spent Fuel Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.123 | 5 | Spent Fuel Building Walls | Spent Fuel Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Spent Fuel Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.2 | 3 | Cool down buildings | Cool down buildings
214.21 | 4 | Cool down building | Cool down building | standard |  |  |  |  | 3295896.8 | [6 empty] | 2025 | Lab and Mat and Equip | fixed cost for now - could work on scaling | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% |  |  | Onsite Learning | 2966307.12 | 4943845.2 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.3 | 3 | Security buildings | Security buildings
214.31 | 4 | Guard station | Guard station | standard |  |  |  |  | 1177108.8 | [6 empty] | 2025 | Lab and Mat and Equip |  | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% |  |  | Onsite Learning | 1059397.92 | 1765663.2 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.4 | 3 | Staff support buildings | Staff support buildings
214.41 | 4 | Staff quarters | Staff quarters | standard |  |  |  |  | 666859.9 | [6 empty] | 2025 | Lab and Mat and Equip | fixed cost for now - could work on scaling | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% |  |  | Onsite Learning | 600173.91 | 1000289.85 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.7 | 3 | Emergency and Start-up Power Systems Building | Emergency and Start-up Power Systems Building
214.71 | 4 | Emergency Building | Emergency Building
214.711 | 5 | Emergency Building Slab Roof | Emergency Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Emergency Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.712 | 5 | Emergency Building Basement | Emergency Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Emergency Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.713 | 5 | Emergency Building Walls | Emergency Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Emergency Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.72 | 4 | Backup Power Outdoor | Backup Power Outdoor
214.721 | 5 | Diesel Generator | Diesel Generator | standard | [5 empty] | 2717311.5663 | $/MWt | Power MWt | 0.083 | MWt | 0.7 | 2024 | Equipment | MARVEL (for the cost of the diesel generator) The exponent is based on the work by Koruoush considering cost scaling from nuclear ad non nuclear power plants. When using the power as scaling variable, the exponent ranges between 0..6 and 0.8 so 0.7 is used here | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Stewart, W. R., & Shirvan, K. (2022). Capital cost estimation for advanced nuclear power plants. Renewable and Sustainable Energy Reviews, 155, 111880. | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf https://www.sciencedirect.com/science/article/pii/S1364032121011473 |  | Factory Other | 0 | 0 | Lognormal | 2445580.4096 | 3532505.0361 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.722 | 5 | Diesel Generator Concrete Pad | Diesel Generator Concrete Pad | standard |  |  |  |  | 20832.7 | [6 empty] | 2025 | Lab and Mat and Equip |  | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% |  |  | Onsite Learning |  |  | Lognormal | 0 | 0 | Lognormal | 0.2 | 1 | 0 | Truncated Normal
214.8 | 3 | Auxilliary Building | Auxilliary Building
214.81 | 4 | Maniplator Building | Maniplator Building
214.811 | 5 | Manipulator Building Slab Roof | Manipulator Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Manipulator Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 | Added a custom building for GCMR based on CAD drawing | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.812 | 5 | ManipulatorBuilding Basement | ManipulatorBuilding Basement | standard | [5 empty] | 943.9 | $/m^3 | Manipulator Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.813 | 5 | Manipulator Building Exterior Walls | Manipulator Building Exterior Walls | standard | [5 empty] | 721.21 | $/m^3 | Manipulator Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.9 | 3 | Encompassing Buildings | Encompassing Buildings
214.91 | 4 | Overarching steel building | Overarching steel building | standard |  |  |  |  | 29675881.9 |  | $/m^2 |  | 2896 | m^2 |  | 2025 | Lab and Mat and Equip |  | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% |  |  | Onsite Learning | 26708293.71 | 44513822.85 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215 | 2 | Supply Chain Buildings | Supply Chain Buildings
215.1 | 3 | Storage Building | Storage Building
215.11 | 4 | Storage Building Slab Roof | Storage Building Slab Roof | standard | [5 empty] | 1200 | $/m^3 | Storage Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1080 | 1560 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.12 | 4 | Storage Building Basement | Storage Building Basement | standard | [5 empty] | 943.9 | $/m^3 | Storage Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 849.51 | 1227.07 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.13 | 4 | Storage Building Walls | Storage Building Walls | standard | [5 empty] | 721.21 | $/m^3 | Storage Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 649.089 | 937.573 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.4 | 3 | Radwaste Building | Radwaste Building
215.41 | 4 | Radwaste Building Slab Roof | Radwaste Building Slab Roof | standard | [5 empty] | 1836 | $/m^3 | Radwaste Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | Onsite Learning | 0 | 0 | Lognormal | 1652.4 | 2386.8 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.42 | 4 | Radwaste Building Basement | Radwaste Building Basement | standard | [5 empty] | 1444.167 | $/m^3 | Radwaste Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 1299.7503 | 1877.4171 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.43 | 4 | Radwaste Building Walls | Radwaste Building Walls | standard | [5 empty] | 1103.4513 | $/m^3 | Radwaste Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip |  |  |  |  | Onsite Learning | 0 | 0 | Lognormal | 993.1062 | 1434.4867 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215.5 | 3 | O&M support buildings | O&M support buildings
215.51 | 4 | O&M support building structure | O&M support building structure | [5 empty] | 1506418.9 | [6 empty] | 2025 | Lab and Mat and Equip | fixed cost for now - could work on scaling | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, average of O&M Support Building and O&M Warehouse, less 30% |  |  | Onsite Learning | 1355777.01 | 2259628.35 | Lognormal | 0 | 0 | Lognormal | 0.0 | 1 | 0 | Truncated Normal
215.52 | 4 | O&M warehouse structure | O&M warehouse structure | standard |  |  |  |  | 2121760.9 | [6 empty] | 2025 | Lab and Mat and Equip | fixed cost for now - could work on scaling | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, average of O&M Support Building and O&M Warehouse, less 30% |  |  | Onsite Learning | 1909584.81 | 3182641.35 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
22 | 1 | Reactor System | Reactor System
221 | 2 | Reactor Components | Reactor Components
221.1 | 3 | Reactor Vessel and Accessories | Reactor Vessel and Accessories
221.11 | 4 | Reactor Support | Reactor Support | standard | [5 empty] | 311.558 | $/Kg | Total Vessels Mass | 2447 | Kg | 0.85 | 2018 | Lab and Mat and Equip | PWR12-ME |  |  | Unit cost is the cost of support structure divided by the cost of guard vessel plus PCS | Factory Primary Structure | 0 | 0 | Lognormal | 280.4022 | 405.0254 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Guard Vessel Material | stainless_steel |  |  |  | 757.2077 | $/Kg | Guard Vessel Mass | 1587 | Kg |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 681.4869 | 984.37 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Guard Vessel Material | low_alloy_steel |  |  |  | 154.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 138.672 | 200.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Guard Vessel Material | incoloy |  |  |  | 444.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 399.672 | 577.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Vessel Material | stainless_steel |  |  | 3369444.6 | 1768.3558 | $/Kg | Vessel Mass | 860 |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  | Unit cost if the PCS cost (in MARVEL) divided by the PCS mass in MARVEL | Factory Primary Structure | 3032500.14 | 5054166.9 | Lognormal | 1591.5202 | 2298.8626 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Vessel Material | low_alloy_steel |  |  |  | 154.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 138.672 | 200.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Vessel Material | incoloy |  |  |  | 444.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  |  | Factory Primary Structure | 0 | 0 | Lognormal | 399.672 | 577.304 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.2 | 3 | Reactor Control Devices | Reactor Control Devices
221.21 | 4 | Reactivity Control System | Reactivity Control System
221.211 | 5 | Reactivity Control System Fabrication | Reactivity Control System Fabrication | standard | [5 empty] | 347890 | $/Drum | Drum Count |  |  |  | 2024 | Lab and Mat and Equip | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team | Gerstner, D., & Arafat, Y. (2023). MARVEL 90% Final Design Report (No. INL/RPT-23-74280-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | The scaling variable here is the total mass of all the control drums | Factory Drums | 0 | 0 | Lognormal | 313101 | 452257 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.212 | 5 | Installation | Installation | standard | [5 empty] | 80665.75 | $/Drum | Drum Count |  |  |  | 2024 | Lab and Equip | MARVEL Project |  |  |  | Factory Drums | 0 | 0 | Lognormal | 72599.175 | 104865.475 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.213 | 5 | Control Drums Materials (Absorber) | Control Drums Materials (Absorber) | standard | Control Drum Absorber | B4C_natural |  |  |  | 14285.7143 | $/Kg | Control Drum Absorber Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Other | 0 | 0 | Lognormal | 12857.1429 | 18571.4286 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.213 | 5 | Control Drums Materials (Absorber) | Control Drums Materials (Absorber) | standard | Control Drum Absorber | B4C_enriched |  |  |  | 10064 | $/Kg | Control Drum Absorber Mass |  |  |  | 2023 | Material | Prosser et al., 2023 |  |  |  | Factory Other | 0 | 0 | Lognormal | 9057.6 | 13083.2 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | BeO |  |  |  | 10062.8931 | $/Kg | Control Drum Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory BeO | 0 | 0 | Lognormal | 9056.6038 | 13081.761 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | Be |  |  |  | 44736.8421 | $/Kg | Control Drum Reflector Mass | 19 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Be | 0 | 0 | Lognormal | 40263.1579 | 58157.8947 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | Graphite |  |  |  | 80 | $/Kg | Control Drum Reflector Mass |  |  |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other | 0 | 0 | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.215 | 5 | Control System Drive Mechanism | Control System Drive Mechanism | standard | [5 empty] | 74759 | $/Drum | Drum Count |  |  |  | 2023 | Lab and Mat and Equip | Prosser et al., 2023 | First-Principles Cost Estimation of a Sodium Fast Reactor Nuclear Plant. INL/RPT-23-74316 Table 38, 39 |  | Bottom-up Estimation of components with nuclear escalation + contingency | Factory Drums | 0 | 0 | Lognormal | 67283.1 | 97186.7 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.216 | 5 | Shutdown Rod Absorber Material | Shutdown Rod Absorber Material | standard | Shutdown Rod Absorber | B4C_natural |  |  |  | 14285.7143 | $/Kg | Shutdown Rod Absorber Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project |  |  | Existing MARVEL natural-B4C cost retained unchanged for shutdown-rod material costing. | Factory Other | 0 | 0 | Lognormal | 12857.1429 | 18571.4286
221.216 | 5 | Shutdown Rod Absorber Material | Shutdown Rod Absorber Material | standard | Shutdown Rod Absorber | B4C_enriched |  |  |  | 10064 | $/Kg | Shutdown Rod Absorber Mass |  | Kg | 1 | 2023 | Material | Prosser et al., 2023 | First-Principles Cost Estimation of a Sodium Fast Reactor Nuclear Plant. INL/RPT-23-74316 |  | Existing enriched-B4C cost retained unchanged for shutdown-rod material costing. | Factory Other | 0 | 0 | Lognormal | 9057.6 | 13083.2
221.217 | 5 | Shutdown Rod Cladding Material | Shutdown Rod Cladding Material | standard | Shutdown Rod Cladding | SS304 |  |  |  | 757.2077 | $/Kg | Shutdown Rod Cladding Mass | 1587 | Kg | 1 | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). |  | Ganda stainless_steel cost used as a proxy for SS304 shutdown-rod cladding. | Factory Other | 0 | 0 | Lognormal | 681.4869 | 984.37
221.3 | 3 | Non-Fuel Core Internals | Non-Fuel Core Internals | standard
221.31 | 4 | Reflector | Reflector
221.311 | 5 | Radial Reflector | Radial Reflector | standard | Radial Reflector | BeO |  |  | 120231 | 10062.8931 | $/Kg | Radial Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team |  |  | Factory BeO | 108207.9 | 180346.5 | Lognormal | 9056.6038 | 13081.761 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.312 | 5 | Axial Reflector | Axial Reflector | standard | Axial Reflector | BeO |  |  | 120231 | 10062.8931 | $/Kg | Axial Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team |  |  | Factory BeO | 108207.9 | 180346.5 | Lognormal | 9056.6038 | 13081.761 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.311 | 5 | Radial Reflector | Radial Reflector | standard | Radial Reflector | Be |  |  |  | 44736.8421 | $/Kg | Radial Reflector Mass | 19 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team |  |  | Factory Be | 0 | 0 | Lognormal | 40263.1579 | 58157.8947 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.312 | 5 | Axial Reflector | Axial Reflector | standard | Axial Reflector | Be |  |  |  | 44736.8421 | $/Kg | Axial Reflector Mass | 19 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team |  |  | Factory Be | 0 | 0 | Lognormal | 40263.1579 | 58157.8947 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.311 | 5 | Radial Reflector | Radial Reflector | standard | Radial Reflector | Graphite |  |  |  | 80 | $/Kg | Radial Reflector Mass |  |  |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other | 0 | 0 | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.312 | 5 | Axial Reflector | Axial Reflector | standard | Axial Reflector | Graphite |  |  |  | 80 | $/Kg | Axial Reflector Mass |  |  |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other | 0 | 0 | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.311 | 5 | Radial Reflector | Radial Reflector | standard | Radial Reflector | Al2O3 |  |  |  | 134.1 | $/Kg | Radial Reflector Mass |  |  |  | 2017 | Material | NTRD-FCO-2018-000439 |  |  |  | Factory Other | 0 | 0 | Lognormal | 120.69 | 174.33 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.312 | 5 | Axial Reflector | Axial Reflector | standard | Axial Reflector | Al2O3 |  |  |  | 134.1 | $/Kg | Axial Reflector Mass |  |  |  | 2017 | Material | NTRD-FCO-2018-000439 |  |  |  | Factory Other | 0 | 0 | Lognormal | 120.69 | 174.33 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.32 | 4 | Shield | Shield
221.321 | 5 | In Vessel Shield Materials | In Vessel Shield Materials | standard | In Vessel Shield Material | B4C_natural |  |  | 647990.6 | 14285.7143 | $/Kg | In Vessel Shield Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Other | 583191.54 | 971985.9 | Lognormal | 12857.1429 | 18571.4286 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.322 | 5 | Out The Vessel Shield Materials | Out The Vessel Shield Materials | standard | Out Of Vessel Shield Material | WEP |  |  |  | 20 | $/Kg | Out Of Vessel Shield Mass | 925.3 | Kg | 1 | 2024 | Material | MARVEL Project |  |  |  | Factory Other | 0 | 0 | Lognormal | 18 | 26 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | Graphite |  |  |  | 80 | $/Kg | Moderator Mass |  | Kg |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other |  |  | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | monolith_graphite |  |  |  | 160 | $/Kg | Moderator Mass |  | Kg |  | 2022 | Material | Monolith graphite is expected to be more expensive so I multiplied the graphite cost by two |  |  |  | Factory Other |  |  | Lognormal | 144 | 208 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | ZrH |  |  |  | 1520 | $/Kg | Moderator Mass |  | Kg |  | 2017 | Material | the Fuel SA&I Cost Basis Report | Abou-Jaoude, A., C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman, N. Stauff, K. Shirvan and A. Stein (2024). Meta-Analysis of Advanced Nuclear Reactor Cost Estimations, Idaho National Laboratory (INL), Idaho Falls, ID (United States). |  |  | Factory Other |  |  | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.33 | 4 | Moderator | Moderator | standard | Moderator | YHx |  |  |  | 1520 | $/Kg | Moderator Mass |  | Kg |  | 2017 | Material |  | We do not know the cost of Yhx. This is just a placeholder for now (assumed to be the same as ZrH) |  |  | Factory Other |  |  | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.34 | 4 | Moderator (Booster) | Moderator (Booster) | standard | Moderator Booster Materials | Graphite |  |  |  | 80 | $/Kg | Moderator Booster Mass Graphite |  | Kg |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference |  |  | Factory Other |  |  | Lognormal | 72 | 104 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.34 | 4 | Moderator (Booster) | Moderator (Booster) | standard | Moderator Booster Materials | YHx |  |  |  | 1520 | $/Kg | Moderator Booster Mass YHx |  | Kg |  | 2017 | Material |  | We do not know the cost of Yhx. This is just a placeholder for now (assumed to be the same as ZrH) |  |  | Factory Other |  |  | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
221.34 | 4 | Moderator (Booster) | Moderator (Booster) | standard | Moderator Booster Materials | ZrH |  |  |  | 1520 | $/Kg | Moderator Booster Mass ZrH |  | Kg |  | 2017 | Material | the Fuel SA&I Cost Basis Report | Abou-Jaoude, A., C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman, N. Stauff, K. Shirvan and A. Stein (2024). Meta-Analysis of Advanced Nuclear Reactor Cost Estimations, Idaho National Laboratory (INL), Idaho Falls, ID (United States). |  |  | Factory Other |  |  | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222 | 2 | Main Heat Transport System | Main Heat Transport System
222.1 | 3 | Fluid Circulation Drive System | Fluid Circulation Drive System
222.11 | 4 | Primary Pump | Primary Pump | nonstandard | Primary Pump | Yes |  |  |  | 8818.5 | $/(kg.sec) | Primary Pump Mechanical Power |  |  | 0.71 | 2003 | Lab and Mat and Equip | Data from non-nuclear power plant + Ratio of safety grade pump nomalized cost compared to non-safety grade pump is btween 10 and 15 (12.5 ratio was used, from the EEDB (Ganda 2019, Figure 23) | Roosen, P., Uhlenbruck, S., & Lucas, K. (2003). Pareto optimization of a combined cycle power system as a decision support tool for trading off investment vs. operating costs. International Journal of Thermal Sciences, 42(6), 553-560. Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). | https://www.sciencedirect.com/science/article/pii/S1290072903000218 https://publications.anl.gov/anlpubs/2019/06/152862.pdf |  | Factory Other | 0 | 0 | Lognormal | 7936.65 | 11464.05 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.12 | 4 | Secondary Pump | Secondary Pump | nonstandard | Secondary Pump | Yes |  |  |  | 705.48 | $/(kg.sec) | Secondary Pump Mechanical Power |  |  | 0.71 | 2003 | Lab and Mat and Equip | Data from non-nuclear power plant |  |  |  | Factory Other | 0 | 0 | Lognormal | 634.932 | 917.124 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.13 | 4 | Compressor | Compressor | nonstandard | reactor type | GCMR |  |  |  | 7100000 | unitless |  |  |  |  | 2020 | Lab and Mat and Equip | ANL/NSE-20/28 | Hoffman et al. (2020). Improvement of ACCERT Algorithm - FY20 (No. ANL/NSE-20/28). Argonne National Laboratory.(ANL), Argonne, IL (United States). |  | Implemented on the python side. Chosen over default due to uncertainty in compressor Pressure Ratio changes based on reactor TH | Factory Other | 0 | 0 | Lognormal | 6390000 | 9230000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.2 | 3 | Reactor Heat Transfer Piping System | Reactor Heat Transfer Piping System | standard | reactor type | GCMR |  |  |  | 20000 | $/MWe | Power MWe |  |  |  | 2017 | Equipment | From EEBD | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 18000 | 26000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.2 | 3 | Reactor Heat Transfer Piping System | Reactor Heat Transfer Piping System | standard | reactor type | LTMR |  |  |  | 20000 | $/MWe | Power MWe |  |  |  | 2017 | Equipment | From EEBD | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 18000 | 26000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.2 | 3 | Reactor Heat Transfer Piping System | Reactor Heat Transfer Piping System | standard | reactor type | HPMR |  |  |  | 10000 | $/heatpipe | Number of Heatpipes | 1 |  | 0.7 | 2017 | Equipment | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_46104.pdf |  |  |  | Factory Other | 0 | 0 | Lognormal | 9000 | 13000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.3 | 3 | Heat Exchangers | Heat Exchangers
222.31 | 4 | Primary Heat Exchanger | Primary Heat Exchanger | standard | HX Material | SS316 |  |  |  | 50 | $/Kg | Primary HX Mass |  | Kg |  | 2004 | Equipment | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology. |  |  | Factory Other | 0 | 0 | Lognormal | 45 | 65 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.31 | 4 | Primary Heat Exchanger | Primary Heat Exchanger | standard | HX Material | 800H |  |  |  | 120 | $/Kg | Primary HX Mass |  | Kg |  | 2013 | Equipment | Non Nuclear Plants | Yoon, S.-J., P. Sabharwall and E.-S. Kim (2013). Analytical study on thermal and mechanical design of printed circuit heat exchanger, Idaho National Lab.(INL), Idaho Falls, ID (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 108 | 156 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger | standard | HX Material | SS316 |  |  |  | 50 | $/Kg | Secondary HX Mass |  | Kg |  | 2004 | Equipment | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology. |  |  | Factory Other | 0 | 0 | Lognormal | 45 | 65 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger | standard | HX Material | 800H |  |  |  | 120 | $/Kg | Secondary HX Mass |  | Kg |  | 2013 | Equipment | Non Nuclear Plants | Yoon, S.-J., P. Sabharwall and E.-S. Kim (2013). Analytical study on thermal and mechanical design of printed circuit heat exchanger, Idaho National Lab.(INL), Idaho Falls, ID (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 108 | 156 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.5 | 3 | Initial Coolant Inventory | Initial Coolant Inventory | standard | Coolant | Helium |  |  |  | 170 | $/Kg | Onsite Coolant Inventory |  | Kg |  | 2024 | Material | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | https://doi.org/10.3929/ethz-b-000709311 | Vendor Quoate (Linde) for 3000 cylinders of 99.999% purity Helium. 3000 cylinders correspond to ~4 MT of He. | No Learning | 0 | 0 | Lognormal | 153 | 221 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.5 | 3 | Initial Coolant Inventory | Initial Coolant Inventory | standard | Coolant | NaK |  |  |  | 118 | $/Kg | Onsite Coolant Inventory |  | Kg |  | 2023 | Material |  |  |  |  | No Learning |  |  |  | 106.2 | 153.4 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.6 | 3 | Integrated Heat Transfer Vessel | Integrated Heat Transfer Vessel |  | reactor type | GCMR
222.61 | 4 | Integrated Heat Transfer Vessel | Integrated Heat Transfer Vessel | standard | reactor type | GCMR |  |  |  | 1768.36 | $/Kg | Integrated Heat Transfer Vessel Mass | 860 | Kg |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  | Custom Accounts to model the vessel that houses the PCHE, Circulator, and Pipe Connections. These are assumed to be SA508 for now but use the same unit-cost as SS PCHE | Factory Other | 0 | 0 | Lognormal | 1591.524 | 2298.868 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222.62 | 4 | Integrated Heat Transfer System Support | Integrated Heat Transfer System Support | standard | reactor type | GCMR |  |  |  | 311.56 | $/Kg | Integrated Heat Transfer Vessel Mass | 2447 | Kg | 0.85 | 2018 | Lab and Mat and Equip | PWR12-ME |  |  |  | Factory Other | 0 | 0 | Lognormal | 280.404 | 405.028 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
223 | 2 | Safety Systems | Safety Systems
223.2 | 3 | Reactor Cavity Cooling System (Rvacs) | Reactor Cavity Cooling System (Rvacs)
223.21 | 4 | Rvacs (Cooling Vessel) | Rvacs (Cooling Vessel) | standard | [5 empty] | 757.2077 | $/Kg | Cooling Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 681.4869 | 984.37 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
223.22 | 4 | Rvacs (Intake Vessel) | Rvacs (Intake Vessel) | standard | [5 empty] | 757.2077 | $/Kg | Intake Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). |  |  | Factory Other | 0 | 0 | Lognormal | 681.4869 | 984.37 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
226 | 2 | Other Reactor Plant Equipment | Other Reactor Plant Equipment | standard | reactor type | LTMR |  |  | 456297 | [6 empty] | 2024 | Equipment | MARVEL |  |  |  | Factory Other | 410667.3 | 684445.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
226 | 2 | Other Reactor Plant Equipment | Other Reactor Plant Equipment | standard | reactor type | GCMR |  |  |  | 118207.7741 | unitless | Primary Loop Mass Flow Rate | 610.21 | kg/s | 0.6 | 2023 | Lab and Mat and Equip | DOE-ET-34222-T1 | 1170 MWt HTGR Steamer Cogeneration Plant Design and Cost Study, United Engineers & Constructors Inc. Philadelphia, Pennsylvania. 1980] | https://www.osti.gov/servlets/purl/5084245 | Cost scalated based on Park et al., 2024 - Bottom-up …. | Factory Other | 0 | 0 | Lognormal | 106386.9966 | 153670.1063 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
227 | 2 | Reactor Instrumentation and Control (I&C) | Reactor Instrumentation and Control (I&C) | standard |  |  |  |  | 8500000 | [6 empty] | 2023 | Lab and Equip | Shirvan et al., 2023 | Shirvan et al,. (2023). UO2-fueled microreactors: Near-term solutions to emerging marktets. Nuclear Engineering and Design. | https://doi.org/10.1016/j.nucengdes.2023.112470 | Cost based on FOAK Digital I&C with 2-out-of-4 voting logic | Non-nuclear off-the-shelf | 7650000 | 12750000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
228 | 2 | Reactor Plant Miscellaneous Items | Reactor Plant Miscellaneous Items | standard |  |  |  |  | 30960 | [6 empty] | 2024 | Lab and Mat and Equip | MARVEL |  |  |  | Factory Other | 27864 | 46440 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23 | 1 | Energy Conversion System | Energy Conversion System
232 | 2 | Energy Applications | Energy Applications
232.1 | 3 | Electricity Generation Systems | Electricity Generation Systems | standard | [5 empty] | 12504 | $/kWe | BoP Power kWe | 1 |  | 0.777 | 2023 | Lab and Mat and Equip | INL/RPT-24-80433 Rev.1 | INL/RPT-24-80433 Rev.1 | https://www.osti.gov/biblio/2447366 |  | Non-nuclear off-the-shelf | 0 | 0 | Lognormal | 11253.6 | 16255.2 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
236 | 2 | Common Instrumentation & Controls | Common Instrumentation & Controls | standard |  |  |  |  | 1000000 | [6 empty] | 2023 | Lab and Mat and Equip |  |  | https://doi.org/10.1016/j.nucengdes.2023.112470 |  | Non-nuclear off-the-shelf | 900000 | 1500000 | Lognormal
24 | 1 | Electrical Equipment | Electrical Equipment
241 | 2 | Switchgear | Switchgear | standard | [5 empty] | 12609.0098 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 11348.1088 | 16391.7127 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
242 | 2 | Station Service Equipment | Station Service Equipment | standard | [5 empty] | 10483.0781 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 9434.7703 | 13628.0016 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
243 | 2 | Switchboards | Switchboards | standard | [5 empty] | 3404.0615 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 3063.6554 | 4425.28 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
244 | 2 | Protective Equipment | Protective Equipment | standard | [5 empty] | 9776.1468 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 8798.5321 | 12708.9908 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
245 | 2 | Electrical Structure & Wiring Container | Electrical Structure & Wiring Container | standard | [5 empty] | 52720.7025 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 47448.6323 | 68536.9133 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
246 | 2 | Power & Control Wiring | Power & Control Wiring | standard | [5 empty] | 39871.5712 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip |  |  |  |  | Non-nuclear off-the-shelf | 0 | 0 |  | 35884.4141 | 51833.0426 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
25 | 1 | Initial Fuel Inventory | Initial Fuel Inventory
251 | 2 | First Core Mining | First Core Mining | standard | [5 empty] | 184 | $/Kg | Natural Uranium Mass |  |  |  | 2022 | Material |  |  |  |  | No Learning | 0 | 0 | Lognormal | 165.6 | 239.2 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
252 | 2 | First Core Conversion | First Core Conversion | standard | [5 empty] | 15.1 | $/Kg | Natural Uranium Mass |  |  |  | 2022 | Material |  |  |  |  | No Learning | 0 | 0 | Lognormal | 13.59 | 19.63 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
253 | 2 | First Core Enrichment | First Core Enrichment | nonstandard | [5 empty] | 184.2 | $/SWU | SWU |  |  | 1 | 2022 | Material |  |  |  |  | No Learning | 0 | 0 | Lognormal | 165.78 | 239.46 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | No | Fuel | TRIGA_fuel |  | 1520 | $/Kg | Uranium Mass |  |  |  | 2023 | Material |  |  |  |  | Factory Other | 0 | 0 | Lognormal | 1368 | 1976 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | No | Fuel | UO2 |  | 250 | $/Kg | Uranium Mass |  |  |  | 2023 | Material |  |  |  |  | Factory Other | 0 | 0 | Lognormal | 225 | 325 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | Yes |  |  |  | 10000 | $/Kg | Uranium Mass |  |  |  | 2009 | Material |  |  |  |  | Factory Other | 0 | 0 | Lognormal | 9000 | 13000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
26 | 1 | Miscellaneous Equipment (Cranes) | Miscellaneous Equipment (Cranes) | standard |  |  |  |  | 1000000 | [6 empty] | 2021 | Equipment | A study for the mass manufacruing and factory fabrication of microreactors | Abou-Jaoude, A., Arafat, Yasir, Foss, Andrew Wilkin, and Dixon, Brent W (2021). An Economics-by-Design Approach Applied to a Heat Pipe Microreactor Concept. 2021. Idaho National Laboratory: Idaho Falls, ID, Idaho National Laboratory. |  |  | Factory Other | 900000 | 1500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
28 | 1 | Dispersed Infrastructure | Dispersed Infrastructure
288.2 | 3 | Security Cameras | Security Cameras | standard |  | 1 |  |  |  | 27507.56 |  | GEN Security Camera Count |  |  |  | 2025 | Equipment |  | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, full cost |  |  | No Learning | 0 | 0 | Lognormal | 24756.804 | 35759.828 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288.3 | 3 | Motion Detectors | Motion Detectors | standard |  | 1 |  |  |  | 23307.56 |  | GEN Motion Detector Count |  |  |  | 2025 | Equipment |  | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, full cost |  |  | No Learning | 0 | 0 | Lognormal | 20976.804 | 30299.828 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288.5 | 3 | Radiation Monitors | Radiation Monitors | standard |  | 1 |  |  |  | 637264.63 |  | GEN Radiation Monitor Count |  |  |  | 2025 | Equipment |  | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, full cost |  |  | Factory Other | 0 | 0 | Lognormal | 573538.167 | 828444.019 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
30 | 0 | Capitalized Indirect Services Cost | Capitalized Indirect Services Cost
31 | 1 | Factory & field indirect costs | Factory & field indirect costs
32 | 1 | Factory and construction supervision | Factory and construction supervision
33 | 1 | Startup Costs | Startup Costs | standard |  |  |  |  | 2407166.4 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 2166449.76 | 3610749.6 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
34 | 1 | Shipping and Transportation Costs | Shipping and Transportation Costs | standard |  |  |  |  | 832641.4 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | Onsite Learning | 749377.26 | 1248962.1 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
35 | 1 | Engineering Services | Engineering Services | standard |  |  |  |  | 620313.5877 | [6 empty] | 2024 | Labor |  |  |  |  | Onsite Learning | 558282.229 | 930470.3816 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
36 | 1 | PM/CM Services | PM/CM Services | standard |  |  |  |  | 416958.936 | [6 empty] | 2024 | Labor |  |  |  |  | Onsite Learning | 375263.0424 | 625438.404 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
40 | 0 | Capitalized training costs | Capitalized training costs
41 | 1 | staff recruitment and training | staff recruitment and training | standard |  |  |  |  | 300000 | [6 empty] | 2024 | Labor |  | Al-Dawood, Khaldoon and Hanna, Botros and Balla, Sai and de Oliveira, Rodrigo and Garcia, Samuel and McCarthy, Dan and Bolisetti, Chandrakanth and Lindley, Ben and Abou-Jaoude, Abdalla, Open-Source Microreactor Design Models for Technoeconomic Assessment. | https://papers.ssrn.com/sol3/papers.cfm?abstract_id=5163464 |  | No Learning | 270000 | 450000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
60 | 0 | Capitalized Financial Costs | Capitalized Financial Costs
62 | 1 | Interest | Interest
70 | 0 | Annualized O&M Cost | Annualized O&M Cost
71 | 1 | O&M Staff | O&M Staff
711 | 2 | Operators | Operators | nonstandard | [5 empty] | 178500 | $/FTE | Number of On-Site Operators per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
712 | 2 | Remote Monitoring Technicians | Remote Monitoring Technicians | nonstandard | Operation Mode | Remotely Monitored |  |  |  | 178500 | $/FTE | Reactors Monitored Per Operator |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
713 | 2 | Security Staff | Security Staff | nonstandard | [5 empty] | 178500 | $/FTE | Security Staff Per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
72 | 1 | Variable Non-Fuel Costs | Variable Non-Fuel Costs
721 | 2 | Coolant | Coolant | nonstandard | Coolant | Helium |  |  |  | 170 | $/Kg | Replacement Coolant Inventory |  | Kg |  | 2024 | Material | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | https://doi.org/10.3929/ethz-b-000709311 | Vendor Quoate (Linde) for 3000 cylinders of 99.999% purity Helium. 3000 cylinders correspond to ~4 MT of He. | No Learning | 0 | 0 | Lognormal | 153 | 221 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
721 | 2 | Coolant | Coolant | nonstandard | Coolant | NaK |  |  |  | 118 | $/Kg | Replacement Coolant Inventory |  | Kg |  | 2023 | Material | MARVEL Project (communication with MARVEL Team) |  |  | Vendor Quotes | No Learning | 0 | 0 | Lognormal | 106.2 | 153.4 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
73 | 1 | Regulatory Costs | Regulatory Costs | standard |  |  |  |  | 107180 | [6 empty] | 2024 | Labor |  |  | https://www.federalregister.gov/documents/2025/02/19/2025-02779/fee-schedules-fee-recovery-for-fiscal-year-2025 |  | Licensing Learning | 96462 | 160770 | Lognormal
75 | 1 | Capital Plant Expenditures | Capital Plant Expenditures
751 | 2 | Annualized Outer Vessel Structure Replacements | Annualized Outer Vessel Structure Replacements
752 | 2 | Annualized Inner Vessel Structure Replacements | Annualized Inner Vessel Structure Replacements
753 | 2 | Annualized Moderator Replacements | Annualized Moderator Replacements
754 | 2 | Annualized Reflector Replacements | Annualized Reflector Replacements
755 | 2 | Annualized Reactor Control Devices Replacements | Annualized Reactor Control Devices Replacements
756 | 2 | Annualized Integrated Heat Transfer Vessel Replacements | Annualized Integrated Heat Transfer Vessel Replacements
757 | 2 | Annualized Moderator Booster Replacements | Annualized Moderator Booster Replacements
759 | 2 | Annualized Plant Maintenance (Misc.) | Annualized Plant Maintenance (Misc.)
759.1 | 3 | Annualized Building and Structural Maintenance (Accounts 212–215) | Annualized Building and Structural Maintenance (Accounts 212–215)
759.2 | 3 | Annualized Main Heat Transport System Maintenance (Accounts 222.1–222.3 and 222.6) | Annualized Main Heat Transport System Maintenance (Accounts 222.1–222.3 and 222.6)
759.3 | 3 | Annualized Safety System Maintenance (Account 223) | Annualized Safety System Maintenance (Account 223)
759.4 | 3 | Annualized Reactor Plant Equipment Maintenance (Accounts 221.11, 226, and 228) | Annualized Reactor Plant Equipment Maintenance (Accounts 221.11, 226, and 228)
759.5 | 3 | Annualized Reactor I&C Maintenance (Account 227) | Annualized Reactor I&C Maintenance (Account 227)
759.6 | 3 | Annualized Energy Conversion System Maintenance (Account 23) | Annualized Energy Conversion System Maintenance (Account 23)
759.7 | 3 | Annualized Electrical Equipment Maintenance (Account 24) | Annualized Electrical Equipment Maintenance (Account 24)
759.8 | 3 | Annualized Miscellaneous Equipment Maintenance (Account 26) | Annualized Miscellaneous Equipment Maintenance (Account 26)
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost | [17 empty] | Implemented on non_direct_cost.py The cost is scaled as a fraction of CAPEX (15%)
80 | 0 | Annualized Fuel Cost | Annualized Fuel Cost
81 | 1 | Refueling Operations | Refueling Operations | nonstandard | [5 empty] | 178500 | $/FTE | Number of On-Site Operators per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
82 | 1 | Additional Nuclear Fuel | Additional Nuclear Fuel
83 | 1 | Spent Fuel Management | Spent Fuel Management | standard | [5 empty] | 1 | $/MWeHour | Annual Electricity Production |  |  | 1 | 2024 | Lab and Mat and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 0.9 | 1.3 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
Note on J68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: check if we're using cost estimators
Note on J80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: replace with cost estimators Reply: overlaps with manipulator building. Remove one of them. Reply: Manipulator building volumes set to zero in my baseline python input file: watts_exec_GCMR_A_H1_height_180_3yr_fleet.py
Note on K140: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to match unit cost of “Inner Vessel Structure” account with material “stainless_steel”. Previous values was $50/kg. I imagine the logic was that the IHX pressure vessel does not need to be nuclear safety graded. Breaking that assumption here. This should make the IHX vessel ~35x more expensive in the current baseline (September 23, 2026).
Note on K141: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to match unit cost of “Reactor Support” account. Previous values was $8/kg. I imagine the logic was that the IHX support does not need to be nuclear safety graded. Breaking that assumption here. (September 23, 2026).

## MARVEL_Cost
Account ID | Account Title | TOTAL COST (2024 USD)
10 | Capitalized Pre-Construction Costs | 5210451
15 | Plant Studies | 5210451
20 | Capitalized Direct Costs | 30295715.422
21 | Structures and Improvements | 2799006.732
211 | Site Preparation/Yard Work
212 | Reactor Island Civil Structures | 2573469.872
213 | Main Function Buildings
214 | Buildings to Support Main Function | 225536.86
214.7 | Emergency and Start-up Power Systems | 225536.86
217 | Miscellaneous Other Structures
22 | Reactor System | 17586712.57
221 | Reactor Components | 8937296.6
221.1 | Reactor vessel and accessories | 2004852
221.11 | Reactor support | 762382.4
221.12 | Outer vessel structure | 1201688.6
221.13 | Inner vessel structure | 40781
221.2 | Reactor control devices | 2114223
221.21 | Reactivity control system | 2114223
221.211 | Reactivity Control System Fabrication | 1391560
221.212 | Installation | 322663
221.213 | Control Drums Materials (Absorber) | 400000
221.214 | Control Drums Materials (Reflector)
221.3 | Non-fuel core internals | 4818221.6
221.31 | Reflector | 4170231
221.311 | Reflector (Materials: BeO) | 3200000
221.312 | Reflector (Materials: Be Metal) | 850000
221.313 | Reflector (installation | 120231
221.32 | Shield | 647990.6
221.33 | Moderator | 0
222 | Main Heat Transport System | 5908950.6
222.1 | Fluid circulation drive system | 0
222.2 | Reactor Heat Hransfer Piping System | 4890230.6
222.21 | Reactor Heat Hransfer Piping System (Mat) | 1520786
222.22 | Reactor Heat Hransfer Piping System (Fabrication) | 3341486
222.23 | Reactor Heat Hransfer Piping System (Installation) | 27958.6
222.3 | Heat Exchangers | 0
222.4 | Pressurizer System | 0
222.5 | Initial Heat Transfer Fluid Inventory | 1018720
224 | Radioactive Byproduct Processing Systems
226 | Other Reactor Plant Equipment | 456297
227 | Reactor Instrumentation and Control (I&C) | 2253208.37
228 | Reactor Plant Miscellaneous Items | 30960
23 | Energy Conversion System | 0
232 | Energy Applications | 0
232.1 | Electricity Generation Systems | 0
24 | Electrical Equipment | 73415.62
244 | Protective Systems Equipment | 1627.02
245 | Electrical Raceway Systems | 0
246 | Power and Control Cables and Wiring | 71788.6
25 | Initial Fuel Inventory | 9836580.5
254 | First Core Fuel Assembly Fabrication | 9836580.5
26 | Miscellaneous Equipment
30 | Capitalized Indirect Services Cost | 6442742.5237
31 | Factory & Field Indirect Costs | 1333020.8
317 | Field Shops | 1333020.8
33 | Startup Costs | 2407166.4
331 | Commissioning and Trial Test Runs | 2407166.4
331.3 | Initial Fuel Loading Operations | 215000
331.5 | Test Runs | 2192166.4
34 | Shipping and Transportation Costs | 1665282.8
341 | Fuel Shipping and Transportation | 1635355.8
345 | Other Shipping and Transportation Costs | 29927
35 | Engineering Services | 620313.5877
351 | Off-Site | 257261.4
352 | On-Site | 363052.1877
36 | PM/CM Services | 416958.936
361 | Off-Site
362 | On-Site | 416958.936
40 | Capitalized Training Costs | 4169765
41 | Staff Recruitment and Training | 4169765
50 | Capitalized Supplementary Costs | 16408781.6
54 | Decommissioning | 16408781.6
60 | Capitalized Financial Costs | 6160606
61 | Escalation | 6160606
70 | Annualized O&M Cost | 2456659.2
71 | O&M Staff | 2456659.2
Non-Recurrung Costs | Non-Recurrung Costs | 33779050.1383

## Design Variables
Variable | Value | Units | Description
Overall System
Thermal power | 83 | kWth | —
Electric Power | 20 | kWe
Core outer radius | 5.5 | inches | —
Reflector outer radius | 16.5 | inches | —
Fuel
Fuel mass | 145.3 | kg | UZrH
U Weight fraction | 30 | wt% | U/UZrH
U enrichment | 19.75 | wt% | High-assay low-enriched uranium (HALEU)
Pins | 36 | # | —
Reflector
Outer reflector material | BeO | — | 99% theoretical density
Elements | 124 | # | Quarter plates
Reflector plate thickness | 1 | inches | —
Reflector plate volume | 818.4 | cm3/plate | —
Mass of BeO reflector | 318 | Kg
Insert volume | 570 | cm3/plate | —
Mass of Be-metal reflector | 0.019 | MT | —
Control Elements
Control drums | 4 | # | —
Shutdown rods | 1 | # | —
Control drum elements | 124 | # | Discs
Drum disc thickness | 1 | inches | —
Drum reflector volume | 880.8 | cm3/plate | BeO 99%
Mass of drum reflector | 309 | Kg | —
Drum poison volume | 49.2 | cm3/plate | B4C
Mass of drum poison | 14 | Kg | —
Mass of rod poison | 14 | Kg | B4C
Instruments and Controls
Control cabinet | 5 |  | —
Instrument cabinet | 2 |  | —
Nuclear input/output (IO) | 9 |  | —
Non-nuclear IO | 213 |  | —
Stirling engine IO | 48 | — | These should be excluded if there no stirling engine?
TOTAL | 277
Shielding in Vessel
Stainless Steel cans | 54.2 | Kg | Stainless Steel cans of the boron carbide shielding material (SS316H)
Gamma shield material | 56.3 | Kg | Gamma shield material inside the guard vessel (of Tungsten)
Neutron shield material in the guard vessel | 39.7 | Kg | made of natural B4C powder and is located above the core (a donut around the core barrel)—
Boron Carbine shielding | 95.3 | Kg | made of natural B4C (called base shield) below the core
Radial (lead) | 2571.9 | Kg | lead
Radial (WEP) | 925.3 | Kg | made of Water Extended Polyster (WEP)
Shielding in Pit
Mass of the pit neutron shielding | 8.3 | MT | Approximated 6-in.-thick covering whole pit and made of Water-extruded poly (WEP)
Heat Transfer
Mass of coolant | 156 | Kg | —
Number of loops | 4 | # | —
Mass of PCSs | 0.86 | MT | SS316H
Subassembly Structure Masses
Reactor support frame | 1.11 | MT | —
Guard vessel | 1.587 | MT | —

## Inflation Adjustment
Year | General | Labor | Material | Equipment | Lab and Mat and Equip | Lab and Equip
1978 | 3.1209 | 4.2536 | 3.811 | 5.3954 | 4.4867 | 4.8245
1985 | 2.538 | 3.3123 | 3.1461 | 4.0604 | 3.5063 | 3.6863
1986 | 2.4878 | 3.2086 | 3.1525 | 3.9571 | 3.4394 | 3.5829
1987 | 2.4278 | 3.1113 | 3.0892 | 3.921 | 3.3738 | 3.5161
1988 | 2.3451 | 2.9898 | 2.9258 | 3.736 | 3.2172 | 3.3629
1989 | 2.2565 | 2.8925 | 2.8323 | 3.5114 | 3.0788 | 3.202
1990 | 2.1749 | 2.7653 | 2.829 | 3.4175 | 3.0039 | 3.0914
1991 | 2.1039 | 2.6562 | 2.811 | 3.3053 | 2.9241 | 2.9807
1992 | 2.0571 | 2.5741 | 2.7622 | 3.1694 | 2.8352 | 2.8717
1993 | 2.0094 | 2.4923 | 2.6314 | 2.9935 | 2.7057 | 2.7429
1994 | 1.9674 | 2.4033 | 2.5281 | 2.9062 | 2.6126 | 2.6548
1995 | 1.927 | 2.3616 | 2.4373 | 2.8565 | 2.5518 | 2.6091
1996 | 1.8924 | 2.3036 | 2.4234 | 2.7958 | 2.5076 | 2.5497
1997 | 1.8603 | 2.2446 | 2.3818 | 2.7306 | 2.4523 | 2.4876
1998 | 1.8396 | 2.1772 | 2.3934 | 2.6719 | 2.4142 | 2.4245
1999 | 1.814 | 2.105 | 2.3704 | 2.655 | 2.3768 | 2.38
2000 | 1.7738 | 2.0073 | 2.3476 | 2.6269 | 2.3273 | 2.3171
2001 | 1.7346 | 1.9172 | 2.3697 | 2.5433 | 2.2768 | 2.2303
2002 | 1.7081 | 1.8543 | 2.3498 | 2.5197 | 2.2413 | 2.187
2003 | 1.6751 | 1.7905 | 2.3003 | 2.4774 | 2.1894 | 2.134
2004 | 1.6313 | 1.7391 | 2.0956 | 2.3858 | 2.0735 | 2.0625
2005 | 1.5816 | 1.6833 | 1.9957 | 2.2928 | 1.9906 | 1.9881
2006 | 1.5343 | 1.6286 | 1.8774 | 2.1163 | 1.8741 | 1.8725
2007 | 1.4938 | 1.5673 | 1.8474 | 1.9427 | 1.7858 | 1.755
2008 | 1.4655 | 1.5132 | 1.7226 | 1.8946 | 1.7102 | 1.7039
2009 | 1.4565 | 1.4969 | 1.7888 | 1.8702 | 1.7186 | 1.6836
2010 | 1.4391 | 1.481 | 1.7398 | 1.8818 | 1.7008 | 1.6814
2011 | 1.41 | 1.4653 | 1.6825 | 1.8042 | 1.6507 | 1.6348
2012 | 1.3842 | 1.4425 | 1.6441 | 1.6867 | 1.5911 | 1.5646
2013 | 1.3611 | 1.4131 | 1.617 | 1.627 | 1.5524 | 1.5201
2014 | 1.3378 | 1.393 | 1.578 | 1.5664 | 1.5125 | 1.4797
2015 | 1.3254 | 1.3645 | 1.5847 | 1.5228 | 1.4907 | 1.4437
2016 | 1.313 | 1.3361 | 1.5821 | 1.5002 | 1.4728 | 1.4182
2017 | 1.2899 | 1.3037 | 1.5268 | 1.4654 | 1.4319 | 1.3845
2018 | 1.261 | 1.2689 | 1.4354 | 1.4136 | 1.3726 | 1.3412
2019 | 1.2402 | 1.2305 | 1.4355 | 1.378 | 1.348 | 1.3042
2020 | 1.2242 | 1.1969 | 1.4148 | 1.3591 | 1.3236 | 1.278
2021 | 1.1706 | 1.1618 | 1.1153 | 1.2995 | 1.1922 | 1.2307
2022 | 1.0934 | 1.1167 | 0.9908 | 1.1498 | 1.0858 | 1.1333
2023 | 1.055 | 1.0707 | 1.0199 | 1.0652 | 1.052 | 1.068
2024 | 1.03 | 1.04 | 1.03 | 1.06 | 1.0433 | 1.05
2025 | 1 | 1 | 1 | 1 | 1 | 1

## Economics Parameters
Parameter | Value | Note | Reference | Notes
indirect to direct field-related cost | 0.06539
FTEs Per Onsite Operator (24/7) | 5
FTEs Per Offsite Operator (24/7) | 5
FTEs Per Security Staff (24/7) | 5
Hours Per FTE | 1800
Work Hours Per Shift | 10
Maintenance to Direct Cost Ratio | 0.03
Onsite Learning | 0.08 | FOAK to NOAK Learning Rates | Assessment of Factory Fabrication Considerations for Nuclear Microreactors 10.1080/00295450.2023.2206779 | Calculated based on Refernce Paper + Gyutae's work. Refer to TEM Slides for rationale and methodology
No Learning | 0
Licensing Learning | 0.2 | Nth of a kind licening was estimated to take 30-42 months https://www.nrc.gov/docs/ML2426/ML24268A310.pdf Now, it is estimated to take 6- 12 months https://www.govinfo.gov/content/pkg/FR-2026-05-01/pdf/2026-08550.pdf Therefor, the cost is estimated to be reduced 4 times (a factor of 0.25). Since MOUSE is using learning rates, this factor is converted to a learning rate of 0.2 assuming 100 units
Factory Primary Structure | 0.18443 | FOAK to NOAK Learning Rates
Factory Drums | 0.24138 | FOAK to NOAK Learning Rates
Factory Other | 0.22963 | FOAK to NOAK Learning Rates
Factory Be | 0.41505 | FOAK to NOAK Learning Rates
Factory BeO | 0.39915 | FOAK to NOAK Learning Rates
Non-nuclear off-the-shelf | 0.05 |  | Park, et al., Bottom-up levelized cost estimation of low-enriched and low-pressure nuclear batteries. Nuclear Engineering and Design. 2025. | For off-the-shelf commercial components that are not produced in the FB Factory
SER Account 30 to Account 20 Ratio | 0.5 |  |  | Account 30 is 50% of direct cost (Account 20).
SER Account 716 to Accounts 711-715 Ratio | 0.02 |  |  | Continuing education and retraining.
SER Account 717 to Accounts 711-715 Ratio | 0.075 |  |  | Management staff.
SER Account 741 to Account 20 Ratio | 0.005 |  |  | Operating chemicals and lubricants.
SER Account 742 to Account 20 Ratio | 0.05 |  |  | Spare parts.
SER Account 743 to Account 20 Ratio | 0.01 |  |  | Utilities excluding electricity, supplies, and consumables.
SER Account 747.1 to Accounts 741-743 Ratio | 0.05 |  |  | Annualized transportation costs.
SER Account 747.4 to Account 20 Ratio | 0.005 |  |  | Annualized other supplies and utilities.
MFG Account 223 to Reactor OCC per Testing Line Ratio | 0.1 |  |  | REVIEW NEEDED: provisional testing-building assumption.
MFG Account 30 to Account 20 Ratio | 0.5 |  |  | Account 30 is 50% of direct cost.
MFG Account 716 to Accounts 711-715 Ratio | 0.02 |  |  | Continuing education and retraining.
MFG Account 717 to Accounts 711-715 Ratio | 0.075 |  |  | Management staff.
MFG Account 741 to Account 20 Ratio | 0.005 |  |  | Operating chemicals and lubricants.
MFG Account 742 to Account 20 Ratio | 0.05 |  |  | Spare parts.
MFG Account 743 to Account 20 Ratio | 0.01 |  |  | Utilities excluding electricity, supplies, and consumables.
MFG Account 747.1 to Accounts 741-743 Ratio | 0.05 |  |  | Annualized transportation costs.
MFG Account 747.4 to Account 20 Ratio | 0.005 |  |  | Annualized other supplies and utilities.

## Manufacturing Campus Database
Account | Level | Account Name | Account Title | Standard Cost Equation? | Count Scaling Variable | Count per Variable | Optional Variable | Optional Value | Fixed Cost ($) | Unit Cost | Unit Cost (units) | Scaling Variable | Scaling Variable Ref Value | Units | Exponent | Dollar Year | Type | Source | Ref | Link | Notes | FOAK to NOAK Multiplier Type | Fixed Cost Low End | Fixed Cost High End | Fixed Cost Distribution | Unit Cost Low End | Unit Cost High End | Unit Cost Distribution | Exponent std | Exponent Max | Exponent Min | Exponent Distribution
10 | 0 | Capitalized Pre-Construction Costs | Capitalized Pre-Construction Costs
11 | 1 | Land Cost | Land Cost | standard | Constant | 1 |  |  |  | 3800 | $/acres | MFG Campus Land Area |  | acres |  | 2022 | General | The average cost per acre for rural land in 2022 from the US Department of Agriculture | Abou-Jaoude, A., Lohse, C. S., Larsen, L. M., Guaita, N., Trivedi, I., Joseck, F. C., ... & Stein, A. (2024). Meta-analysis of advanced nuclear reactor cost estimations (No. INL/RPT-24-77048-Rev001). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_107010.pdf |  | No Learning | 0 | 0 | Lognormal | 3420 | 4940 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
12 | 1 | Site Permits | Site Permits | standard | Constant | 1 |  |  |  | 10030 | $/MWe | MFG Campus Power |  | MWe |  | 2022 | Labor | Data from SMR MHTGRs |  |  |  | No Learning | 0 | 0 | Lognormal | 9027 | 13039 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
13 | 1 | Plant Licensing | Plant Licensing | standard | Constant | 1 |  |  | 45000000 | [6 empty] | 2009 | Labor | NGNP project | Gandrik, A., B. Wallace, L. Demick, S. Melancon and M. Patterson (2011). "Assessment of high temperature gas-cooled reactor (HTGR) capital and operating costs." Idaho National Laboratory, TEV-1196, Idaho Falls, ID. | https://art.inl.gov/NGNP/INL%20Documents/Year%202012/Assessment%20of%20High%20Temperature%20Gas-Cooled%20Reactor%20-%20HTGR%20-%20Capital%20and%20Operating%20Costs.pdf |  | No Learning | 45000000 | 70000000 | Uniform | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
14 | 1 | Plant Permits | Plant Permits | standard | Constant | 1 |  |  | 3000000 | [6 empty] | 2009 | Labor | NGNP project |  |  |  | No Learning | 2700000 | 4500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
15 | 1 | Plant Studies | Plant Studies | standard | Constant | 1 |  |  | 52104510 | [6 empty] | 2024 | Labor | MARVEL Project (Labor-adjusted Cost) | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf | MARVEL's data were updated | No Learning | 46894059 | 78156765 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
20 | 0 | Capitalized Direct Costs | Capitalized Direct Costs | [18 empty] | 598
21 | 1 | Structures and Improvements | Structures and Improvements
211 | 2 | Site Preparation/ Yard Work | Site Preparation/ Yard Work
211.1 | 3 | Cleaning and Grubbing | Cleaning and Grubbing | standard | Constant | 1 |  |  |  | 5862.8794 | $/acres | MFG Campus Land Area |  | acres |  | 2024 | Lab and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | No Learning | 0 | 0 | Lognormal | 5276.5915 | 7621.7432 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.2 | 3 | Stripping Topsoil | Stripping Topsoil | standard | Constant | 1 |  |  |  | 3411.716 | $/acres | MFG Campus Land Area |  | acres |  | 2024 | Lab and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 3070.5444 | 4435.2308 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.4 | 3 | Roads | Roads | standard | Constant | 1 |  |  |  | 8867.5852 | $/m | MFG Road Length | 1 |  | 1 | 2025 | General | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 7980.8266 | 11527.8607 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.9 | 3 | Security Fencing | Security Fencing
211.91 | 4 | Security Fencing Limited | Security Fencing Limited | standard | Constant | 1 |  |  |  | 191.1 | $/ft | MFG Site Perimeter |  |  |  | 2025 | Lab and Equip | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 171.99 | 248.43 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.93 | 4 | Security Fencing Protected | Security Fencing Protected | standard | Constant | 1 |  |  |  | 11022.2 | $/ft | MFG Protected Perimeter |  |  |  | 2025 | Lab and Equip | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 9919.98 | 14328.86 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214 | 2 | Servicing Facilities Structures | Servicing Facilities Structures
214.3 | 3 | Control Buidlings | Control Buidlings
214.31 | 4 | Local Control Buidling Structure | Local Control Buidling Structure | standard | Constant | 1 |  |  |  | 19989.1719 | $/m^2 | MFG Local Control Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 17990.2547 | 25985.9235 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
22 | 1 | Main Facilities Estimated As Wholes | Main Facilities Estimated As Wholes
221 | 2 | Manufacturing Building | Manufacturing Building | standard | [5 empty] | 62733.0281 |  | Production Rate | 1000 | Rx/yr | 0.13827 | 2025 | Lab and Mat and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 56459.7253 | 81552.9365 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222 | 2 | Fueling Building | Fueling Building | standard | [5 empty] | 35766.9719 |  | Production Rate | 1000 | Rx/yr | 0.13827 | 2025 | Lab and Mat and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 32190.2747 | 46497.0635 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
223 | 2 | Testing Building | Testing Building | [18 empty] | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
224 | 2 | Warehouse | Warehouse | standard | [5 empty] | 3842.71 | $/m^2 | MFG Warehouse Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 3458.439 | 4995.523 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
225 | 2 | Administrative Building | Administrative Building | standard | [5 empty] | 14828.0024 | $/m^2 | MFG Administration Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 13345.2021 | 19276.4031 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23 | 1 | Equipment | Equipment
23.5 | 2 | Local Integrated Control Rooms | Local Integrated Control Rooms | standard | MFG Testing Line Count | 1 |  |  | 8500000 | [6 empty] | 2023 | Lab and Equip | Shirvan et al., 2023 | Shirvan et al,. (2023). UO2-fueled microreactors: Near-term solutions to emerging marktets. Nuclear Engineering and Design. | https://doi.org/10.1016/j.nucengdes.2023.112470 | Cost based on FOAK Digital I&C with 2-out-of-4 voting logic | Factory Other | 0 | 12750000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
28 | 1 | Auxiliary Infrastructure Equipment | Auxiliary Infrastructure Equipment
281 | 2 | Emergency Power | Emergency Power | standard | [5 empty] | 3500000 | $/MWe | MFG Emergency Generator Power | 1 | MWe | 1 | 2025 | Equipment | 2.5 MW generator cost from Central States Generators, nuclear multiple of 5, and guess for pad and connection to building (pad and connection have been requested with cost estimators)
283 | 2 | Fire Station | Fire Station | standard | MFG Fire Station Count | 1 |  |  | 14543550 | [6 empty] | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 21815325 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
284 | 2 | Security Building | Security Building | standard | [5 empty] | 19198.0437 | $/m^2 | MFG Security Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 17278.2393 | 24957.4568 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
285 | 2 | Switchyard | Switchyard | standard | [5 empty] | 516717.0237 | $/MWe | MFG Switchyard Rating | 300 | MWe | 0.9968 | 2025 | Lab and Mat and Equip | Scaling relationship created from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 465045.3213 | 671732.1308 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
286 | 2 | Onsite Transport Equipment | Onsite Transport Equipment
286.1 | 3 | Local Reactor Transport Vehicles | Local Reactor Transport Vehicles | standard | MFG Local Transport Vehicle Count | 1 |  |  | 938000 | [6 empty] | 2023 | Equipment | Lallemant report, Table 9, Considered price for 200 MT LTV | Lallemant, Lucas. 2023 |  |  | No Learning | 844200 | 1407000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
286.2 | 3 | Utility Vehicles | Utility Vehicles | standard | MFG Utility Vehicle Count | 1 |  |  | 50000 | [6 empty] | 2024 | Equipment | assumption |  |  |  | No Learning | 45000 | 75000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288 | 2 | Dispered Infrastructure | Dispered Infrastructure | [14 empty] | assumption, guess
288.1 | 3 | Communication | Communication | standard | [5 empty] | 11774.5787 | $/acres | Manufacturing Campus Area | 1068 | acres |  | 2025 | Equipment | [to become a scaling relationship] MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf
288.2 | 3 | Security Cameras | Security Cameras | standard | MFG Security Camera Count | 1 |  |  | 28431 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf
288.3 | 3 | Motion Detectors | Motion Detectors | standard | MFG Motion Detector Count | 1 |  |  | 24057 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf
288.4 | 3 | Guard Station | Guard Station | standard | MFG Guard Station Count | 1 |  |  | 6774250 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf
30 | 0 | Capitalized Indirect Services Cost | Capitalized Indirect Services Cost
40 | 0 | Capitalized training costs | Capitalized training costs
41 | 1 | staff recruitment and training | staff recruitment and training | standard | Constant | 1 |  |  | 300000 | [6 empty] | 2024 | Labor |  |  |  |  | No Learning | 270000 | 450000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
60 | 0 | Capitalized Financial Costs | Capitalized Financial Costs
62 | 1 | Interest | Interest
70 | 0 | Annualized O&M Cost | Annualized O&M Cost
71 | 1 | O&M Staff | O&M Staff
711 | 2 | Operators (Testing Only) | Operators (Testing Only) | nonstandard | [5 empty] | 178500 | $/FTE | MFG Testing Number of Operators |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
712 | 2 | Warehouse Staff | Warehouse Staff | nonstandard | [5 empty] | 113000 | $/FTE | MFG Warehouse Staff |  |  | 1 | 2024 | Labor | Average of four occupations from Munro work: Forklift Drivers, Supervisors, Shipping/receiving personnel, and Materials Scheduler (high ends for all) | INL Fueling - Manufacturing Parts and Equipment List Rev002.xlsx |  |  | No Learning | 0 | 0 | Lognormal | 101700 | 146900 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
713 | 2 | Security Staff | Security Staff | nonstandard | [5 empty] | 178500 | $/FTE | MFG Security Staff Per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
714 | 2 | Maintenance Staff | Maintenance Staff | nonstandard | [5 empty] | 178500 | $/FTE | MFG Maintenance Staff Headcount |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
715 | 2 | Engineering Staff (Testing Only) | Engineering Staff (Testing Only) | nonstandard | [5 empty] | 200000 | $/FTE | MFG Testing Engineering Headcount |  |  |  | 2024 | Labor |  |  |  |  | No Learning | 0 | 0 | Lognormal | 180000 | 260000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
716 | 2 | Continuing Education and Staff Retraining | Continuing Education and Staff Retraining | [13 empty] | Labor |  |  |  |  | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
717 | 2 | Management Staff | Management Staff | [13 empty] | Labor |  |  |  |  | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
718 | 2 | Manfuacturing Building Staff | Manfuacturing Building Staff | standard | [5 empty] | 2838754.3735 | unitless | Production Rate | 1 | Rx/yr | 0.14704 | 2025 | Labor |  |  |  |  | No Learning | 0 | 0 | Lognormal | 2554878.9362 | 3690380.6856 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
719 | 2 | Fueling Building Staff | Fueling Building Staff | standard | [5 empty] | 699358.8575 | unitless | Production Rate | 1 | Rx/yr | 0.29939 | 2025 | Labor |  |  |  |  | No Learning | 0 | 0 | Lognormal | 629422.9717 | 909166.5147 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
74 | 1 | Fixed O&M Utilities and Materials | Fixed O&M Utilities and Materials
741 | 2 | Operating Chemicals and Lubricants (Except Manufacturing and Fueling) | Operating Chemicals and Lubricants (Except Manufacturing and Fueling) | [18 empty] | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
742 | 2 | Spare Parts (Except Manufacturing and Fueling) | Spare Parts (Except Manufacturing and Fueling) | [18 empty] | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
743 | 2 | Utilities except electricity, Supplies, and Consumables | Utilities except electricity, Supplies, and Consumables | [18 empty] | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
744 | 2 | Electricity | Electricity | nonstandard | Constant | 1 |  |  |  | 90 | $/MWeHour | MFG Campus Power |  |  | 1 | 2025 | General |  |  |  |  | No Learning | 0 | 0 | Lognormal | 81 | 117 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
745 | 2 | Manufacturing Building Equipment | Manufacturing Building Equipment | standard | [5 empty] | 405910.1934 | unitless | Production Rate | 1 | Rx/yr | 0.12689 | 2025 | Equipment |  |  |  |  | No Learning | 0 | 0 | Lognormal | 365319.1741 | 527683.2514 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
746 | 2 | Fueling Building Equipment | Fueling Building Equipment | standard | [5 empty] | 82100.2961 | unitless | Production Rate | 1 | Rx/yr | 0.15955 | 2025 | Equipment |  |  |  |  | No Learning | 0 | 0 | Lognormal | 73890.2665 | 106730.385 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747 | 2 | Other annual costs | Other annual costs | [18 empty] | No Learning | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.1 | 3 | Annualized Transportation Costs | Annualized Transportation Costs | [19 empty] | 0 | 0 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.3 | 3 | Annualized Helium Replenishment | Annualized Helium Replenishment | standard | Production Rate | 1 |  |  |  | 170 | $/Kg | MFG Testing Coolant Allotment |  | Kg |  | 2024 | Equipment | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | https://doi.org/10.3929/ethz-b-000709311 | Vendor Quoate (Linde) for 3000 cylinders of 99.999% purity Helium. 3000 cylinders correspond to ~4 MT of He. | No Learning | 0 | 0 | Lognormal | 153 | 221 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.4 | 3 | Annualized Other Supplies and Utilities | Annualized Other Supplies and Utilities | [18 empty] | No Learning |  |  | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
75 | 1 | Capital Plant Expenditures | Capital Plant Expenditures
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost

## Servicing Campus Database
Account | Level | Account Name | Account Title | Standard Cost Equation? | Count Scaling Variable | Count per Variable | Optional Variable | Optional Value | Fixed Cost ($) | Unit Cost | Unit Cost (units) | Scaling Variable | Scaling Variable Ref Value | Units | Exponent | Dollar Year | Type | Source | Ref | Link | Notes | FOAK to NOAK Multiplier Type | Fixed Cost Low End | Fixed Cost High End | Fixed Cost Distribution | Unit Cost Low End | Unit Cost High End | Unit Cost Distribution | Exponent std | Exponent Max | Exponent Min | Exponent Distribution
10 | 0 | Capitalized Pre-Construction Costs | Capitalized Pre-Construction Costs
11 | 1 | Land Cost | Land Cost | standard | Constant | 1 |  |  |  | 3800 | $/acres | SER Campus Area |  | acres |  | 2022 | General | The average cost per acre for rural land in 2022 from the US Department of Agriculture | Abou-Jaoude, A., Lohse, C. S., Larsen, L. M., Guaita, N., Trivedi, I., Joseck, F. C., ... & Stein, A. (2024). Meta-analysis of advanced nuclear reactor cost estimations (No. INL/RPT-24-77048-Rev001). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_107010.pdf |  | No Learning | 0 | 0 | Lognormal | 3420 | 4940 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
12 | 1 | Site Permits | Site Permits | standard | Constant | 1 |  |  |  | 10030 | $/MWe | SER Switchyard Rating |  | MWe |  | 2022 | Labor | Data from SMR MHTGRs |  |  |  | No Learning | 0 | 0 | Lognormal | 9027 | 13039 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
13 | 1 | Plant Licensing | Plant Licensing | standard | Constant | 1 |  |  | 57500000 | [6 empty] | 2009 | Labor | NGNP project | Gandrik, A., B. Wallace, L. Demick, S. Melancon and M. Patterson (2011). "Assessment of high temperature gas-cooled reactor (HTGR) capital and operating costs." Idaho National Laboratory, TEV-1196, Idaho Falls, ID. | https://art.inl.gov/NGNP/INL%20Documents/Year%202012/Assessment%20of%20High%20Temperature%20Gas-Cooled%20Reactor%20-%20HTGR%20-%20Capital%20and%20Operating%20Costs.pdf |  | No Learning | 45000000 | 70000000 | Uniform | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
14 | 1 | Plant Permits | Plant Permits | standard | Constant | 1 |  |  | 3000000 | [6 empty] | 2009 | Labor | NGNP project |  |  |  | No Learning | 2700000 | 4500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
15 | 1 | Plant Studies | Plant Studies | standard | Constant | 1 |  |  | 52104510 | [6 empty] | 2024 | Labor | MARVEL Project (Labor-adjusted Cost) | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf | MARVEL's data were updated | No Learning | 46894059 | 78156765 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
20 | 0 | Capitalized Direct Costs | Capitalized Direct Costs | [18 empty] | 598
21 | 1 | Structures and Improvements | Structures and Improvements
211 | 2 | Site Preparation/ Yard Work | Site Preparation/ Yard Work
211.1 | 3 | Cleaning and Grubbing | Cleaning and Grubbing | standard | Constant | 1 |  |  |  | 5862.8794 | $/acres | SER Campus Land Area |  | acres |  | 2024 | Lab and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857 |  | No Learning | 0 | 0 | Lognormal | 5276.5915 | 7621.7432 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.2 | 3 | Stripping Topsoil | Stripping Topsoil | standard | Constant | 1 |  |  |  | 3411.716 | $/acres | SER Campus Land Area |  | acres |  | 2024 | Lab and Equip |  |  |  |  | No Learning | 0 | 0 | Lognormal | 3070.5444 | 4435.2308 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.4 | 3 | Roads | Roads | standard | Constant | 1 |  |  |  | 8867.5852 | $/m | SER Road Length | 1 |  | 1 | 2025 | General | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 7980.8266 | 11527.8607 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.9 | 3 | Security Fencing | Security Fencing
211.91 | 4 | Security Fencing Limited | Security Fencing Limited | standard | Constant | 1 |  |  |  | 191.1 | $/ft | SER Site Perimeter |  |  |  | 2025 | Lab and Equip | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 171.99 | 248.43 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.92 | 4 | Security Fencing Controlled | Security Fencing Controlled | standard | Constant | 1 |  |  |  | 229.6 | $/ft | SER Controlled Perimeter |  |  |  | 2025 | Lab and Equip | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 206.64 | 298.48 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
211.93 | 4 | Security Fencing Protected | Security Fencing Protected | standard | Constant | 1 |  |  |  | 11022.2 | $/ft | SER Protected Perimeter |  |  |  | 2025 | Lab and Equip | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 9919.98 | 14328.86 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214 | 2 | Servicing Facilities Structures | Servicing Facilities Structures
214.1 | 3 | Servicing Building | Servicing Building
214.11 | 4 | Servicing Hot Cell Building Structure | Servicing Hot Cell Building Structure | standard | Constant | 1 |  |  |  | 25078.8385 | $/m^2 | Servicing Hot Cell Building Area | 31493.7816 | m^2 | 0.95139 | 2025 | Lab and Mat and Equip | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 20063.0708 | 50157.677 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.2 | 3 | Helium Purification and Storage Building
214.21 | 4 | Helium Purification and Storage Building Structure | Helium Purification and Storage Building Structure | standard | Constant | 1 |  |  |  | 21995.1716 | $/m^2 | Helium Purification and Storage Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 19795.6544 | 28593.723 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.3 | 3 | Control Buidlings | Control Buidlings
214.31 | 4 | Local Control Building Structure | Local Control Building Structure | standard | Constant | 1 |  |  |  | 19989.1719 | $/m^2 | SER Local Control Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 17990.2547 | 25985.9235 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.32 | 4 | Remote Control Center Structure | Remote Control Center Structure | standard | Constant | 1 |  |  |  | 17382.2162 | $/m^2 | SER Remote Control Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 15643.9946 | 22596.881 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.4 | 3 | Radioactive Waste Processing Building | Radioactive Waste Processing Building
214.41 | 4 | Radioactive Waste Processing Building Structure | Radioactive Waste Processing Building Structure | standard | Constant | 1 |  |  |  | 46864.9262 | $/m^2 | SER Rad Waste Management Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 42178.4336 | 60924.404 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.6 | 3 | Used Fuel Storage Pads | Used Fuel Storage Pads | standard | [5 empty] | 6171250 | $/(reactors/year) | Servicing Rate | 1 | reactors/year | 1 | 2009 | Lab and Mat and Equip | Value for 40,000 MTU option in Cost Estimate for an Away-From-Reactor Generic Interim Storage Facility (GISF) for Spent Nuclear Fuel, EPRI report 1018722 |  | https://www.epri.com/research/products/1018722 |  | No Learning | 0 | 0 | Lognormal | 5554125 | 8022625 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
214.7 | 3 | Rad Waste Storage Warehouses | Rad Waste Storage Warehouses | standard | [5 empty] | 8448.3448 | $/m^2 | Radwaste Storage Warehouses Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | MC30 Cost Estimation of Microreactor Facilities Rev 1 Draft Backup Info 8-5-2026.xlsx, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 7603.5103 | 10982.8482 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
215 | 2 | Air Tranport Hangar | Air Tranport Hangar
215.1 | 3 | Air Transport Hangar | Air Transport Hangar | standard |  |  |  |  | 10000000 | [6 empty] | 2024 | Equipment | none |  |  |  | No Learning | 0 | 15000000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
22 | 1 | Main Facilities Estimated As Wholes | Main Facilities Estimated As Wholes
221 | 2 | Reactor Cask Management Yard and Inspection Shop | Reactor Cask Management Yard and Inspection Shop | standard | [5 empty] | 41875.218 |  | Servicing Rate | 300 | Rx/yr | 0.25048 | 2025 | Lab and Mat and Equip | Scaling relationship created from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 37687.6962 | 54437.7834 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
222 | 2 | Vehicle Depot and Mechanic Shop | Vehicle Depot and Mechanic Shop | standard | [5 empty] | 135561.195 |  | Servicing Rate | 300 | m^2 | 0.26666 | 2025 | Lab and Mat and Equip | Scaling relationship created from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 122005.0755 | 176229.5535 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
224 | 2 | Parts Service Center and Warehouse | Parts Service Center and Warehouse | standard | [5 empty] | 50000 | $/m^2 | Parts Service Center and Warehouse Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | Judgement |  |  |  | No Learning | 0 | 0 | Lognormal | 45000 | 65000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
225 | 2 | Administrative Building | Administrative Building | standard | [5 empty] | 14247.0882 | $/m^2 | SER Administration Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 12822.3794 | 18521.2147 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23 | 1 | Equipment | Equipment
23.1 | 2 | Servicing Hot Cell | Servicing Hot Cell | standard | Servicing Hot Cell Count | 1 |  |  | 1000000000 | [6 empty] | 2024 | Lab and Mat and Equip | assumption |  |  |  | No Learning | 0 | 2000000000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23.2 | 2 | Helium Purification Equipment | Helium Purification Equipment | standard | Constant | 1 |  |  |  | 963000000 |  | SER Helium Flowrate | 0.055556 | kg/s | 0.6 | 2024 | Lab and Mat and Equip | 0.6 is assumption. Cost is an average of the range given on p. 115 of the Ref. ((4700000+6000000)/2), and flowrate is 200 kg/h as given on p. 113 in the caption of Table 48. | Fernandez de Losada, Lucas Javier. Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. (Master's thesis, ETH Zurich, 2024). https://doi.org/10.3929/ethz-b-000709311 | https://doi.org/10.3929/ethz-b-000709311 |  | No Learning | 0 | 0 | Lognormal | 866700000 | 1251900000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23.4 | 2 | Radioactive Waste Processing Hot Cell | Radioactive Waste Processing Hot Cell | standard | Radioactive Waste Processing Hot Cell Count | 1 |  |  | 1000000000 | [6 empty] | 2024 | Equipment | assumption |  |  | Should process 5 generating sites' worth of radwaste | No Learning | 0 | 2000000000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23.5 | 2 | Local Integrated Control Rooms | Local Integrated Control Rooms | standard | Servicing Hot Cell Count | 1 |  |  | 10777635 | [6 empty] | 1987 | Lab and Mat and Equip | One-half the cost of the Reactor Instrumentation + Control System of the PWR-12-BE from the EEDB | Report on the ACCERT Cost Algorithms Tool, ANL/NSE-19/10 | https://publications.anl.gov/anlpubs/2019/06/152862.pdf |  | No Learning | 0 | 16166452.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23.6 | 2 | Remote Control Rooms | Remote Control Rooms | standard | Constant | 1 |  |  |  | 1000000 |  | Generating Sites Count |  |  |  | 2024 | Lab and Mat and Equip | Assumption: $1 million per reactor, to approximately match Enrique's engineering judgment that a total cost of the remote control room of $1 billion per 1,000 reactors monitored would be reasonable. |  |  |  | No Learning | 0 | 0 | Lognormal | 900000 | 1300000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
23.8 | 2 | Reactor Transport Casks | Reactor Transport Casks | standard | Constant | 1 |  |  | 10000000 |  |  | Reactor Transport Cask Count |  |  |  | 2024 | Lab and Mat and Equip | assumption |  |  |  | No Learning | 0 | 15000000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
28 | 1 | Auxiliary Infrastructure Equipment | Auxiliary Infrastructure Equipment
281 | 2 | Emergency Power | Emergency Power | standard | [5 empty] | 3500000 | $/MWe | SER Emergency Generator Power | 1 | MWe | 1 | 2025 | Equipment | 2.5 MW generator cost from Central States Generators, nuclear multiple of 5, and guess for pad and connection to building (pad and connection have been requested with cost estimators) |  |  |  | No Learning | 0 | 0 | Lognormal | 3150000 | 4550000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
282 | 2 | Service Air Water Building | Service Air Water Building | standard | Service Air Water Building Count | 1 |  |  | 15090300 | [6 empty] | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 22635450 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
283 | 2 | Fire Station | Fire Station | standard | SER Fire Station Count | 1 |  |  | 14543550 | [6 empty] | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 21815325 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
284 | 2 | Security Building | Security Building | standard | [5 empty] | 19198.0437 | $/m^2 | SER Security Building Area | 1 | m^2 | 1 | 2025 | Lab and Mat and Equip | 100 value from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% [temporary, want to add scaling equation] |  |  |  | No Learning | 0 | 0 | Lognormal | 17278.2393 | 24957.4568 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
285 | 2 | Switchyard | Switchyard | standard | [5 empty] | 516717.0237 | $/MWe | SER Switchyard Rating | 300 | MWe | 0.9968 | 2025 | Lab and Mat and Equip | Scaling relationship created from MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf, less 30% |  |  |  | No Learning | 0 | 0 | Lognormal | 465045.3213 | 671732.1308 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
286 | 2 | Onsite Transport Equipment | Onsite Transport Equipment
286.1 | 3 | Local Reactor Transport Vehicles | Local Reactor Transport Vehicles | standard | SER Local Transport Vehicle Count | 1 |  |  | 938000 | [6 empty] | 2023 | Equipment | Lallemant report, Table 9, Considered price for 200 MT LTV | Lallemant, Lucas. 2023 |  |  | No Learning | 844200 | 1407000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
286.2 | 3 | Utility Vehicles | Utility Vehicles | standard | SER Utility Vehicle Count | 1 |  |  | 50000 | [6 empty] | 2024 | Equipment | assumption |  |  |  | No Learning | 45000 | 75000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
287 | 2 | Offsite Transport Equipment | Offsite Transport Equipment
287.1 | 3 | Reactor Transport Vehicles | Reactor Transport Vehicles | standard | Reactor Transport Vehicle Count | 1 |  |  | 1000000 | [6 empty] | 2024 | Equipment | assumption |  |  |  | No Learning | 900000 | 1500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
287.2 | 3 | Helium Transport Trucks | Helium Transport Trucks | standard | Helium Transport Truck Count | 1 |  |  | 500000 | [6 empty] | 2024 | Equipment | assumption |  |  |  | No Learning | 450000 | 750000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
287.3 | 3 | Water Tanker Trucks | Water Tanker Trucks | standard | Water Tanker Truck Count | 1 |  |  | 300000 | [6 empty] | 2024 | Equipment | assumption |  |  |  | No Learning | 270000 | 450000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
287.4 | 3 | Maintenance Trucks | Maintenance Trucks | standard | Maintenance Truck Count | 1 |  |  | 500000 | [6 empty] | 2024 | Equipment | assumption |  |  |  | No Learning | 450000 | 750000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
287.5 | 3 | Air Transport Equipment | Air Transport Equipment
287.51 | 4 | Heavy Lift Helicopters | Heavy Lift Helicopters | standard | Helicopter Count | 1 |  |  | 50000000 | [6 empty] | 2024 | Equipment | none |  |  |  | No Learning | 45000000 | 75000000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
287.52 | 4 | Aircraft Maintenance Equipment | Aircraft Maintenance Equipment | standard | Constant | 1 |  |  | 1000000 | [6 empty] | 2024 | Equipment | none |  |  |  | No Learning | 900000 | 1500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288 | 2 | Dispered Infrastructure | Dispered Infrastructure | [14 empty] | assumption, guess
288.1 | 3 | Communication | Communication | standard | [5 empty] | 11774.5787 | $/acres | SER Campus Land Area | 1068 | acres |  | 2025 | Equipment | [to become a scaling relationship] MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf |  |  |  | No Learning | 0 | 0 | Lognormal | 10597.1208 | 15306.9522 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288.2 | 3 | Security Cameras | Security Cameras | standard | SER Security Camera Count | 1 |  |  | 28431 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf |  |  |  | No Learning | 25587.9 | 42646.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288.3 | 3 | Motion Detectors | Motion Detectors | standard | SER Motion Detector Count | 1 |  |  | 24057 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf |  |  |  | No Learning | 21651.3 | 36085.5 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288.4 | 3 | Guard Station | Guard Station | standard | SER Guard Station Count | 1 |  |  | 6774250 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf |  |  |  | No Learning | 6096825 | 10161375 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
288.5 | 3 | Radiation Monitors | Radiation Monitors | standard | SER Radiation Monitor Count | 1 |  |  | 656100 | [6 empty] | 2025 | Equipment | MC30 Cost Estimation of Microreactor Facilities Inital Draft 5-6-2026.pdf |  |  |  | No Learning | 590490 | 984150 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
30 | 0 | Capitalized Indirect Services Cost | Capitalized Indirect Services Cost
40 | 0 | Capitalized training costs | Capitalized training costs
41 | 1 | staff recruitment and training | staff recruitment and training | standard | Constant | 1 |  |  | 300000 | [6 empty] | 2024 | Labor |  |  |  |  | No Learning | 270000 | 450000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
60 | 0 | Capitalized Financial Costs | Capitalized Financial Costs
62 | 1 | Interest | Interest
70 | 0 | Annualized O&M Cost | Annualized O&M Cost
71 | 1 | O&M Staff | O&M Staff
711 | 2 | Operators | Operators | nonstandard |  | 1 |  |  |  | 178500 | $/FTE-year | SER Operator FTEs Per Facility |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
712 | 2 | Remote Monitoring Technicians | Remote Monitoring Technicians | nonstandard | Reactors Monitored Per Operator | 1 |  |  |  | 178500 | $/FTE | Generating Sites Count |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
713 | 2 | Security Staff | Security Staff | nonstandard | Shift To Headcount | 1 |  |  |  | 178500 | $/FTE | SER Security Staff Per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
714 | 2 | Maintenance Staff | Maintenance Staff | nonstandard | Shift To Headcount | 1 |  |  |  | 178500 | $/FTE | SER Maintenance Staff Per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511. |  |  | No Learning | 0 | 0 | Lognormal | 160650 | 232050 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
715 | 2 | Engineering Staff | Engineering Staff | nonstandard | [5 empty] | 200000 | $/FTE | SER Engineering Headcount |  |  |  | 2024 | Labor |  |  |  |  | No Learning | 0 | 0 | Lognormal | 180000 | 260000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
716 | 2 | Continuing Education and Staff Retraining | Continuing Education and Staff Retraining | [13 empty] | Labor |  |  |  |  | No Learning | 0 | 0 |  | 0 | 0
717 | 2 | Management Staff | Management Staff | [13 empty] | Labor |  |  |  |  | No Learning | 0 | 0 |  | 0 | 0
74 | 1 | Fixed O&M Utilities and Materials | Fixed O&M Utilities and Materials
741 | 2 | Operating Chemicals and Lubricants | Operating Chemicals and Lubricants | [18 empty] | No Learning | 0 | 0 |  | 0 | 0
742 | 2 | Spare Parts | Spare Parts | [18 empty] | No Learning | 0 | 0 |  | 0 | 0
743 | 2 | Utilities except electricity, Supplies, and Consumables | Utilities except electricity, Supplies, and Consumables | [18 empty] | No Learning | 0 | 0 |  | 0 | 0
744 | 2 | Electricity | Electricity | nonstandard | Constant | 1 |  |  |  | 90 | $/MWeHour | SER Switchyard Average Power |  |  | 1 | 2025 | General |  |  |  |  | No Learning | 0 | 0 | Lognormal | 81 | 117 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.1 | 3 | Annualized Transportation Costs | Annualized Transportation Costs | [18 empty] | No Learning | 0 | 0 |  | 0 | 0
747.2 | 3 | Annualized Cask Replacements | Annualized Cask Replacements
747.21 | 4 | Used Fuel Cask | Used Fuel Cask | standard | Annual Used Fuel Cask Consumption | 1 |  |  | 1159000 | [6 empty] | 2023 | Equipment | MIT-ANP-TR-198 |  |  | NUHOMS EOS 37 PTH ESC Cask | No Learning | 1008000 | 1310000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.22 | 4 | Reactor Transport Cask | Reactor Transport Cask | standard | Annual Reactor Cask Replacement | 1 |  |  | 10000000 | [6 empty] | 2024 | Lab and Mat and Equip | assumption | 0 | 0 | 0 | No Learning | 0 | 15000000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.23 | 4 | Radwaste Storage Cask | Radwaste Storage Cask | standard | Annual Radwaste Cask Consumption | 1 |  |  | 1159000 | [6 empty] | 2023 | Equipment | MIT-ANP-TR-198 |  |  | NUHOMS EOS 37 PTH ESC Cask | No Learning | 1008000 | 1310000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.24 | 4 | Used Fuel Storage Additional Overpacks | Used Fuel Storage Additional Overpacks | standard | [5 empty] | 200000 | $/(reactors/year) | Servicing Rate | 1 | reactors/year | 1 | 2009 | Equipment |  |  | https://doi.org/10.3929/ethz-b-000709311 |  | No Learning | 0 | 0 | Lognormal | 160000 | 400000 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.3 | 3 | Annualized Helium Replenishment | Annualized Helium Replenishment | standard | Constant | 1 |  |  |  | 170 | $/Kg | He Gas Replenishment |  | Kg |  | 2024 | Equipment | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | Fernandez de Losada. (2024). Assessment of the Lifecycle Cost of Nuclear-Grade Coolants for Advanced Reactors. ETHzurich. Swiss. | https://doi.org/10.3929/ethz-b-000709311 | Vendor Quoate (Linde) for 3000 cylinders of 99.999% purity Helium. 3000 cylinders correspond to ~4 MT of He. | No Learning | 0 | 0 | Lognormal | 153 | 221 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.4 | 3 | Annualized Other Supplies and Utilities | Annualized Other Supplies and Utilities
747.5 | 3 | Servicing Vehicle O&M | Servicing Vehicle O&M
747.51 | 4 | Reactor Transport Vehicles O&M | Reactor Transport Vehicles O&M | standard | Reactor Transport Vehicle Count | 1 |  |  | 8200000 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | No Learning | 7380000 | 12300000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.52 | 4 | Helium Transport Trucks O&M | Helium Transport Trucks O&M | standard | Helium Transport Truck Count | 1 |  |  | 1300000 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | No Learning | 1170000 | 1950000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.53 | 4 | Water Tanker Trucks O&M | Water Tanker Trucks O&M | standard | Water Tanker Truck Count | 1 |  |  | 1200000 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | No Learning | 1080000 | 1800000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
747.54 | 4 | Maintenance Trucks O&M | Maintenance Trucks O&M | standard | Maintenance Truck Count | 1 |  |  | 5000000 | [6 empty] | 2024 | Lab and Equip |  |  |  |  | No Learning | 4500000 | 7500000 | Lognormal | 0 | 0 | Lognormal | 0.1 | 1 | 0 | Truncated Normal
75 | 1 | Capital Plant Expenditures | Capital Plant Expenditures
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost
Note on K35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Increased ~13.5x to match Enrique’s engineering judgement of how much this service center should cost. (September 23, 2026)
Note on K39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Multiplied by 10 to reflect Enrique’s engineering judgement that this system should be an order-of-magnitude more expensive because it’s receiving dirty helium from reactors that do NOT have continuous purification. (September 23, 2026)