## Cost Database
Account | Level | Account Name | Account Title | Standard Cost Equation? | Optional Variable | Optional Value | Fixed Cost ($) | Unit Cost | Unit Cost (units) | Scaling Variable | Scaling Variable Ref Value | Units | Exponent | Dollar Year | Type | Source | Ref | Link | Notes
10 | 0 | Capitalized Pre-Construction Costs | Capitalized Pre-Construction Costs
11 | 1 | Land Cost | Land Cost | standard |  |  |  | 3800 | $/acres | Land Area |  | acres |  | 2022 | General | The average cost per acre for rural land in 2022 from the US Department of Agriculture | Abou-Jaoude, A., Lohse, C. S., Larsen, L. M., Guaita, N., Trivedi, I., Joseck, F. C., ... & Stein, A. (2024). Meta-analysis of advanced nuclear reactor cost estimations (No. INL/RPT-24-77048-Rev001). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_107010.pdf
12 | 1 | Site Permits | Site Permits | standard |  |  |  | 10030 | $/MWe | Power MWe |  | MWe |  | 2022 | Labor | Data from SMR MHTGRs
13 | 1 | Plant Licensing | Plant Licensing | standard |  |  | 50000000 | [6 empty] | 2009 | Labor | NGNP project | Gandrik, A., B. Wallace, L. Demick, S. Melancon and M. Patterson (2011). "Assessment of high temperature gas-cooled reactor (HTGR) capital and operating costs." Idaho National Laboratory, TEV-1196, Idaho Falls, ID. | https://art.inl.gov/NGNP/INL%20Documents/Year%202012/Assessment%20of%20High%20Temperature%20Gas-Cooled%20Reactor%20-%20HTGR%20-%20Capital%20and%20Operating%20Costs.pdf
14 | 1 | Plant Permits | Plant Permits | standard |  |  | 3000000 | [6 empty] | 2009 | Labor | NGNP project
15 | 1 | Plant Studies | Plant Studies | standard |  |  | 5210451 | [6 empty] | 2024 | Labor | MARVEL Project (Labor-adjusted Cost) | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf | MARVEL's data were updated
20 | 0 | Capitalized Direct Costs | Capitalized Direct Costs
21 | 1 | Structures and Improvements | Structures and Improvements
211 | 2 | Site Preparation/ Yard Work | Site Preparation/ Yard Work
211.1 | 3 | Cleaning and Grubbing | Cleaning and Grubbing | standard |  |  |  | 5862.8794 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
211.2 | 3 | Stripping Topsoil | Stripping Topsoil | standard |  |  |  | 3411.716 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip
211.3 | 3 | Excavation | Excavation | standard |  |  |  | 32.004 | $/m^3 | Excavation Volume |  | m^3 |  | 2024 | Lab and Equip
212 | 2 | Reactor Island Civil Structures | Reactor Island Civil Structures
212.1 | 3 | Reactor Building Slab Roof | Reactor Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Reactor Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
212.2 | 3 | Reactor Building Basement | Reactor Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Reactor Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
212.3 | 3 | Reactor Building Walls | Reactor Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Reactor Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
213 | 2 | Main Function Buildings | Main Function Buildings
213.1 | 3 | Energy conversion Building | Energy conversion Building
213.11 | 4 | Energy Conversion Building Slab Roof | Energy Conversion Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Turbine Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
213.12 | 4 | Energy Conversion Building Basement | Energy Conversion Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Turbine Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
213.13 | 4 | Energy Conversion Building Walls | Energy Conversion Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Turbine Building Exterior Wall |  | m^3 |  | 2024 | Lab and Mat and Equip
213.2 | 3 | Control building | Control building
213.21 | 4 | Control Building Slab Roof | Control Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Control Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
213.22 | 4 | Control Building Basement | Control Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Control Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
213.23 | 4 | Control Building Walls | Control Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Control Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214 | 2 | Buildings to Support Main Function | Buildings to Support Main Function
214.1 | 3 | Fuel Management Buildings | Fuel Management Buildings
214.11 | 4 | Refueling Building | Refueling Building
214.111 | 5 | Refueling Building Slab Roof | Refueling Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Refueling Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
214.112 | 5 | Refueling Building Basement | Refueling Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Refueling Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.113 | 5 | Refueling Building Walls | Refueling Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Refueling Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.12 | 4 | Spent Fuel Building | Spent Fuel Building
214.121 | 5 | Spent Fuel Building Slab Roof | Spent Fuel Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Spent Fuel Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
214.122 | 5 | Spent Fuel Building Basement | Spent Fuel Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Spent Fuel Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.123 | 5 | Spent Fuel Building Walls | Spent Fuel Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Spent Fuel Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.7 | 3 | Emergency and Start-up Power Systems Building | Emergency and Start-up Power Systems Building
214.71 | 4 | Emergency Building | Emergency Building
214.711 | 5 | Emergency Building Slab Roof | Emergency Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Emergency Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
214.712 | 5 | Emergency Building Basement | Emergency Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Emergency Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.713 | 5 | Emergency Building Walls | Emergency Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Emergency Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.72 | 4 | Diesel Generator | Diesel Generator | standard |  |  |  | 2717311.5663 | $/MWt | Power MWt | 0.083 | MWt | 0.7 | 2024 | Equipment | MARVEL (for the cost of the diesel generator) The exponent is based on the work by Koruoush considering cost scaling from nuclear ad non nuclear power plants. When using the power as scaling variable, the exponent ranges between 0..6 and 0.8 so 0.7 is used here | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Stewart, W. R., & Shirvan, K. (2022). Capital cost estimation for advanced nuclear power plants. Renewable and Sustainable Energy Reviews, 155, 111880. | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf https://www.sciencedirect.com/science/article/pii/S1364032121011473
215 | 2 | Supply Chain Buildings | Supply Chain Buildings
215.1 | 3 | Storage Building | Storage Building
215.11 | 4 | Storage Building Slab Roof | Storage Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Storage Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
215.12 | 4 | Storage Building Basement | Storage Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Storage Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
215.13 | 4 | Storage Building Walls | Storage Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Storage Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
215.4 | 3 | Radwaste Building | Radwaste Building
215.41 | 4 | Radwaste Building Slab Roof | Radwaste Building Slab Roof | standard |  |  |  | 1836 | $/m^3 | Radwaste Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
215.42 | 4 | Radwaste Building Basement | Radwaste Building Basement | standard |  |  |  | 1444.167 | $/m^3 | Radwaste Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
215.43 | 4 | Radwaste Building Walls | Radwaste Building Walls | standard |  |  |  | 1103.4513 | $/m^3 | Radwaste Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
22 | 1 | Reactor System | Reactor System
221 | 2 | Reactor Components | Reactor Components
221.1 | 3 | Reactor Vessel and Accessories | Reactor Vessel and Accessories
221.11 | 4 | Reactor Support | Reactor Support | standard |  |  |  | 8.1938 | $/Kg | Total Vessels Mass | 387000 | Kg | 0.85 | 2018 | Lab and Mat and Equip | PWR12-ME |  |  | Unit cost is the cost of support structure divided by the cost of guard vessel plus PCS
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Outer Vessel Material | SS316 |  | 324.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States).
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Outer Vessel Material | SA508 |  | 154.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure | standard | Outer Vessel Material | 800H |  | 444.08 | $/Kg | Guard Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Inner Vessel Material | SS316 |  | 324.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 |  |  | Unit cost if the PCS cost (in MARVEL) divided by the PCS mass in MARVEL
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Inner Vessel Material | SA508 |  | 154.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure | standard | Inner Vessel Material | 800H |  | 444.08 | $/Kg | Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018
221.2 | 3 | Reactor Control Devices | Reactor Control Devices
221.21 | 4 | Reactivity Control System | Reactivity Control System
221.211 | 5 | Reactivity Control System Fabrication | Reactivity Control System Fabrication | standard |  |  | 1391560 | [5 empty] | 1 | 2024 | Lab and Mat and Equip | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team | Gerstner, D., & Arafat, Y. (2023). MARVEL 90% Final Design Report (No. INL/RPT-23-74280-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | The scaling variable here is the total mass of all the control drums
221.212 | 5 | Installation | Installation | standard |  |  |  | 80665.75 | $/Drum | Control Drum Count |  |  |  | 2024 | Lab and Equip | MARVEL Project
221.213 | 5 | Control Drums Materials (Absorber) | Control Drums Materials (Absorber) | standard | Control Drum Absorber | B4C_natural |  | 14285.7143 | $/Kg | Control Drum Absorber Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project
221.213 | 5 | Control Drums Materials (Absorber) | Control Drums Materials (Absorber) | standard | Control Drum Absorber | B4C_enriched |  | 10064 | $/Kg | Control Drum Absorber Mass |  |  |  | 2023 | Material | Prosser et al., 2023
221.214 | 5 | Control Drums Materials (Reflector) | Control Drums Materials (Reflector) | standard | Control Drum Reflector | BeO |  | 10062.8931 | $/Kg | Control Drum Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project
221.215 | 5 | Control System Drive Mechanism | Control System Drive Mechanism | standard |  |  |  | 74759 | $/Drum | Control Drum Count |  |  |  | 2023 | Lab and Mat and Equip | Prosser et al., 2023 | First-Principles Cost Estimation of a Sodium Fast Reactor Nuclear Plant. INL/RPT-23-74316 Table 38, 39 |  | Bottom-up Estimation of components with nuclear escalation + contingency
221.3 | 3 | Non-Fuel Core Internals | Non-Fuel Core Internals | standard
221.31 | 4 | Reflector | Reflector | standard | Reflector | BeO | 120231 | 10062.8931 | $/Kg | Reflector Mass | 318 | Kg | 1 | 2024 | Material | MARVEL Project | Updated MARVEL Cost Estimate + Communication with MARVEL Team | Gerstner, D., & Arafat, Y. (2023). MARVEL 90% Final Design Report (No. INL/RPT-23-74280-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States).
221.31 | 4 | Reflector | Reflector | standard | Reflector | Graphite |  | 80 | $/Kg | Reflector Mass |  |  |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference
221.31 | 4 | Reflector | Reflector | standard | Reflector | Al2O3 |  | 134.1 | $/Kg | Reflector Mass |  |  |  | 2017 | Material | NTRD-FCO-2018-000439
221.32 | 4 | Shield | Shield
221.321 | 5 | In Vessel Shield Materials | In Vessel Shield Materials | standard | In Vessel Shielding Material | B4C_natural | 647990.6 | 14285.7143 | $/Kg | In Vessel Shielding Mass | 28 | Kg | 1 | 2024 | Material | MARVEL Project
221.322 | 5 | Out The Vessel Shield Materials | Out The Vessel Shield Materials | standard | Out Of Vessel Shielding Material | WEP |  | 20 | $/Kg | Out Of Vessel Shielding Mass | 925.3 | Kg | 1 | 2024 | Material | MARVEL Project
221.33 | 4 | Moderator | Moderator | standard | Moderator | ZrH |  | 1520 | $/Kg | Moderator Mass |  | Kg |  | 2017 | Material | the Fuel SA&I Cost Basis Report | Abou-Jaoude, A., C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman, N. Stauff, K. Shirvan and A. Stein (2024). Meta-Analysis of Advanced Nuclear Reactor Cost Estimations, Idaho National Laboratory (INL), Idaho Falls, ID (United States).
221.33 | 4 | Moderator | Moderator | standard | Moderator | Graphite |  | 80 | $/Kg | Moderator Mass |  | Kg |  | 2022 | Material | Naranjo de Candido and Shirvan, 2022 | Naranjo De Candido and Shirvan. (2022). Graphite Life-Cycle Cost Model for HTGRs, International High-Level Radioactive Waste Management Conference
222 | 2 | Main Heat Transport System | Main Heat Transport System
222.1 | 3 | Fluid Circulation Drive System | Fluid Circulation Drive System
222.11 | 4 | Primary Pump | Primary Pump | nonstandard | Primary Pump | Yes |  | 8818.5 | $/(kg.sec) | Primary Pump Mechanical Power |  |  | 0.71 | 2003 | Equipment | Data from non-nuclear power plant + Ratio of safety grade pump nomalized cost compared to non-safety grade pump is btween 10 and 15 (12.5 ratio was used, from the EEDB (Ganda 2019, Figure 23) | Roosen, P., Uhlenbruck, S., & Lucas, K. (2003). Pareto optimization of a combined cycle power system as a decision support tool for trading off investment vs. operating costs. International Journal of Thermal Sciences, 42(6), 553-560. Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States). | https://www.sciencedirect.com/science/article/pii/S1290072903000218 https://publications.anl.gov/anlpubs/2019/06/152862.pdf
222.12 | 4 | Secondary Pump | Secondary Pump | nonstandard | Secondary Pump | Yes |  | 705.48 | $/(kg.sec) | Secondary Pump Mechanical Power |  |  | 0.71 | 2003 | Equipment | Data from non-nuclear power plant
222.13 | 4 | Compressor | Compressor | nonstandard | reactor type | GCMR | [9 empty] | ANL/NSE-20/28 | Hoffman et al. (2020). Improvement of ACCERT Algorithm - FY20 (No. ANL/NSE-20/28). Argonne National Laboratory.(ANL), Argonne, IL (United States). |  | Implemented on the python side
222.2 | 3 | Reactor Heat Transfer Piping System | Reactor Heat Transfer Piping System | standard |  |  |  | 20000 | $/MWe | Power MWe |  |  |  | 2017 | Equipment | From EEBD | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States).
222.3 | 3 | Heat Exchangers | Heat Exchangers
222.31 | 4 | Primary Heat Exchanger | Primary Heat Exchanger | standard | HX Material | SS316 |  | 50 | $/Kg | Primary HX Mass |  | Kg |  | 2004 | Equipment | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology.
222.31 | 4 | Primary Heat Exchanger | Primary Heat Exchanger | standard | HX Material | 800H |  | 120 | $/Kg | Primary HX Mass |  | Kg |  | 2013 | Equipment | Non Nuclear Plants | Yoon, S.-J., P. Sabharwall and E.-S. Kim (2013). Analytical study on thermal and mechanical design of printed circuit heat exchanger, Idaho National Lab.(INL), Idaho Falls, ID (United States).
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger | standard | HX Material | SS316 |  | 50 | $/Kg | Secondary HX Mass |  | Kg |  | 2004 | Equipment | Non Nuclear Plants | Gezelius, K. (2004). Design of compact intermediate heat exchangers for gas cooled fast reactors, Massachusetts Institute of Technology.
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger | standard | HX Material | 800H |  | 120 | $/Kg | Secondary HX Mass |  | Kg |  | 2013 | Equipment | Non Nuclear Plants | Yoon, S.-J., P. Sabharwall and E.-S. Kim (2013). Analytical study on thermal and mechanical design of printed circuit heat exchanger, Idaho National Lab.(INL), Idaho Falls, ID (United States).
223 | 2 | Safety Systems | Safety Systems
223.2 | 3 | Reactor Cavity Cooling System (Rvacs) | Reactor Cavity Cooling System (Rvacs)
223.21 | 4 | Rvacs (Cooling Vessel) | Rvacs (Cooling Vessel) | standard | RVACS Scaling | RVACS Mass |  | 324.08 | $/Kg | Cooling Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States).
223.21 | 4 | Rvacs (Cooling Vessel) | Rvacs (Cooling Vessel) | standard | RVACS Scaling | RPV Surface Area |  | 114006.2469 | unitless | RPV Surface Area | 150.8 | m^2 | 1.21 | 2023 | Lab and Mat and Equip | Venneri, 2023
223.22 | 4 | Rvacs (Intake Vessel) | Rvacs (Intake Vessel) | standard | RVACS Scaling | RVACS Mass |  | 324.08 | $/Kg | Intake Vessel Mass |  |  |  | 2017 | Lab and Mat and Equip | Ganda et al., 2018 | Ganda, F., Hoffman, E., Taiwo, T. A., Kim, T. K., & Hansen, J. (2019). Report on the ACCERT cost algorithms tool (No. ANL/NSE-19/10). Argonne National Lab.(ANL), Argonne, IL (United States).
226 | 2 | Other Reactor Plant Equipment | Other Reactor Plant Equipment | standard | reactor type | HPCR | 456297 | [6 empty] | 2024 | Equipment | MARVEL
226 | 2 | Other Reactor Plant Equipment | Other Reactor Plant Equipment | standard | reactor type | GCMR |  | 118207.7741 | unitless | Primary Mass Flow Rate | 610.21 | kg/s | 0.6 | 2023 | Lab and Mat and Equip | DOE-ET-34222-T1 | 1170 MWt HTGR Steamer Cogeneration Plant Design and Cost Study, United Engineers & Constructors Inc. Philadelphia, Pennsylvania. 1980] | https://www.osti.gov/servlets/purl/5084245 | Cost scalated based on Park et al., 2024 - Bottom-up ….
227 | 2 | Reactor Instrumentation and Control (I&C) | Reactor Instrumentation and Control (I&C) | standard |  |  | 8500000 | [6 empty] | 2023 | Lab and Equip | Shirvan et al., 2023 | Shirvan et al,. (2023). UO2-fueled microreactors: Near-term solutions to emerging marktets. Nuclear Engineering and Design. | https://doi.org/10.1016/j.nucengdes.2023.112470 | Cost based on FOAK Digital I&C with 2-out-of-4 voting logic
228 | 2 | Reactor Plant Miscellaneous Items | Reactor Plant Miscellaneous Items | standard |  |  | 30960 | [6 empty] | 2024 | Lab and Mat and Equip | MARVEL
23 | 1 | Energy Conversion System | Energy Conversion System
232 | 2 | Energy Applications | Energy Applications
232.1 | 3 | Electricity Generation Systems | Electricity Generation Systems | standard |  |  |  | 12504 | $/kWe | Power kWe | 1 | kWe | 0.777 | 2023 | Lab and Mat and Equip | INL/RPT-24-80433 Rev.1 | INL/RPT-24-80433 Rev.1 | https://www.osti.gov/biblio/2447366
236 | 2 | Common Instrumentation & Controls | Common Instrumentation & Controls | standard |  |  | 1000000 | [7 empty] | Lab and Mat and Equip | Shirvan et al., 2023 | Shirvan et al,. (2023). UO2-fueled microreactors: Near-term solutions to emerging marktets. Nuclear Engineering and Design. | https://doi.org/10.1016/j.nucengdes.2023.112470
24 | 1 | Electrical Equipment | Electrical Equipment
241 | 2 | Switchgear | Switchgear | standard |  |  |  | 12609.0098 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip | EEDB PWR12-ME + Stewart and Shirvan (2022) Scales PWR12-ME costs with simplifications based on Stewart and Srhivan (2022) | Stewart, W. R., & Shirvan, K. (2022). Capital cost estimation for advanced nuclear power plants. Renewable and Sustainable Energy Reviews, 155, 111880.
242 | 2 | Station Service Equipment | Station Service Equipment | standard |  |  |  | 10483.0781 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip
243 | 2 | Switchboards | Switchboards | standard |  |  |  | 3404.0615 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip
244 | 2 | Protective Equipment | Protective Equipment | standard |  |  |  | 9776.1468 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip
245 | 2 | Electrical Structure & Wiring Container | Electrical Structure & Wiring Container | standard |  |  |  | 52720.7025 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip
256 | 2 | Power & Control Wiring | Power & Control Wiring | standard |  |  |  | 39871.5712 | $/MWe | Power MWe | 1144 | MWe | 0.6 | 2018 | Lab and Mat and Equip
25 | 1 | Initial Fuel Inventory | Initial Fuel Inventory
251 | 2 | First Core Mining | First Core Mining | standard |  |  |  | 184 | $/Kg | Natural Uranium Mass |  |  |  | 2022 | Material | INL Cost Basis Report & Meta analysis for the nuclear reactor costs | Abou-Jaoude, Abdalla, et al. Meta-Analysis of Advanced Nuclear Reactor Cost Estimations. No. INL/RPT-24-77048-Rev001. Idaho National Laboratory (INL), Idaho Falls, ID (United States), 2024. Abou-Jaoude, A., Y. Arafat, A. Foss, and B. Dixon. 2021. “An Economics-by-Design Approach Applied to a Heat Pipe Microreactor Concept.” INL/EXT-21-63067, Rev. 000, Idaho National Laboratory, Idaho Falls, Idaho. https://doi.org/10.2172/1811894.
252 | 2 | First Core Conversion | First Core Conversion | standard |  |  |  | 15.1 | $/Kg | Natural Uranium Mass |  |  |  | 2022 | Material
253 | 2 | First Core Enrichment | First Core Enrichment | nonstandard |  |  |  | 184.2 | $/SWU | SWU |  |  | 1 | 2022 | Material
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | No |  | 1520 | $/Kg | Uranium Mass |  |  |  | 2023 | Material
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication | standard | TRISO Fueled | Yes |  | 10000 | $/Kg | Uranium Mass |  |  |  | 2009 | Material
26 | 1 | Miscellaneous Equipment (Cranes) | Miscellaneous Equipment (Cranes) | standard |  |  | 1000000 | [6 empty] | 2021 | Equipment | A study for the mass manufacruing and factory fabrication of microreactors | Abou-Jaoude, A., Arafat, Yasir, Foss, Andrew Wilkin, and Dixon, Brent W (2021). An Economics-by-Design Approach Applied to a Heat Pipe Microreactor Concept. 2021. Idaho National Laboratory: Idaho Falls, ID, Idaho National Laboratory.
30 | 0 | Capitalized Indirect Services Cost | Capitalized Indirect Services Cost
31 | 1 | Factory & field indirect costs | Factory & field indirect costs
32 | 1 | Factory and construction supervision | Factory and construction supervision
33 | 1 | Startup Costs | Startup Costs | standard |  |  | 2407166.4 | [6 empty] | 2024 | Lab and Equip | MARVEL
34 | 1 | Shipping and Transportation Costs | Shipping and Transportation Costs | standard |  |  | 1665282.8 | [6 empty] | 2024 | Lab and Equip
35 | 1 | Engineering Services | Engineering Services | standard |  |  | 620313.5877 | [6 empty] | 2024 | Labor
36 | 1 | PM/CM Services | PM/CM Services | standard |  |  | 416958.936 | [6 empty] | 2024 | Labor
40 | 0 | Capitalized training costs | Capitalized training costs
41 | 1 | staff recruitment and training | staff recruitment and training | standard |  |  | 4169765 | [6 empty] | 2024 | Labor | MARVEL
60 | 0 | Capitalized Financial Costs | Capitalized Financial Costs
62 | 1 | Interest | Interest
70 | 0 | Annualized O&M Cost | Annualized O&M Cost
71 | 1 | O&M Staff | O&M Staff
711 | 2 | Operators | Operators | nonstandard |  |  |  | 178500 | $/FTE | Number of Operators |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511.
712 | 2 | Remote Monitoring Technicians | Remote Monitoring Technicians | nonstandard | Operation Mode | Autonomous |  | 178500 | $/FTE | Reactors Monitored Per Operator |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511.
713 | 2 | Security Staff | Security Staff | nonstandard |  |  |  | 178500 | $/FTE | Security Staff Per Shift |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511.
72 | 1 | Variable Non-Fuel Costs | Variable Non-Fuel Costs | nonstandard | reactor type | GMCR
75 | 1 | Capital Plant Expenditures | Capital Plant Expenditures | nonstandard | reactor type | GCMR
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost | nonstandard | Estimation Method | Power Normalized |  | 1144000 | $/MWe | Power MWe |  |  | 1 | 2024 | Lab and Equip |  | Abou-Jaoude, A., C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman, N. Stauff, K. Shirvan and A. Stein (2024). Meta-Analysis of Advanced Nuclear Reactor Cost Estimations, Idaho National Laboratory (INL), Idaho Falls, ID (United States).
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost | nonstandard | Estimation Method | CAPEX Fraction |  | 0.15 | unitless
80 | 0 | Annualized Fuel Cost | Annualized Fuel Cost
81 | 1 | Refueling Operations | Refueling Operations | nonstandard |  |  |  | 178500 | $/FTE | Number of Operators |  |  | 1 | 2024 | Labor |  | de Candido, I., A. Al Rashdan, A. Abou-Jaoude, and J. Buongiorno. 2024. “Assessment of Technoeconomic Opportunities in Automation for Nuclear Microreactors.” Nuclear Science and Engineering, 1–20. https://doi.org/10.1080/00295639.2024.2372511.
82 | 1 | Additional Nuclear Fuel | Additional Nuclear Fuel
83 | 1 | Spent Fuel Management | Spent Fuel Management | standard |  |  |  | 1 | $/MWeHour | Annual Electricity Production |  |  | 1 | 2024 | Lab and Mat and Equip
Note on L68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since the cost of the BeO of the drums was not available, the cost of the BeO reflector is divided by its mass to get a unit cost for the BeO
Note on A69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Added control rod/drum drive mechanism. Assuming: 1drum:1drive n_rod:1drive (Reactor design dependent) Reply: Ganda 2018: reports a cost of 610,000 $/drive (based on CE 1978 LMFBR cost), which is also quoted by Sai
Note on A71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Todo: Update when we get feedback on BeO/Be costs
Note on L75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cost data about B4C are based on the B4C of the control drums
Note on J81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The primary pump needs to be expensive!!
Note on I96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline Cost: 8844770 1978USD Escalation (to 2023): 8.155
Note on C133: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Variable costs that are not fuel-based, such as borated water, control rods, burnable poisons, and other consumable Reply: For the GCMR, likley includes replacement coolant, CO2 refill, etc.
Note on C134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Upgrades to maintain or improve plant capacity, meet future regulatory requirements, or plant life extensions. These costs are considered "sustaining capital" for continued plant operation and performance. Reply: Will allocate vessel, internals, IHX replacement, etc.

## MARVEL_Cost
Account ID | Account Title | TOTAL COST (2024 USD)
10 | Capitalized Pre-Construction Costs | 5210451
15 | Plant Studies | 5210451
20 | Capitalized Direct Costs | 30295715.422
21 | Structures and Improvements | 2799006.732
211 | Site Preparation/Yard Work
212 | Reactor Island Civil Structures | 2573469.872
213 | Main Function Buildings
214 | Buildings to Support Main Function | 225536.86
214.7 | Emergency and Start-up Power Systems | 225536.86
217 | Miscellaneous Other Structures
22 | Reactor System | 17586712.57
221 | Reactor Components | 8937296.6
221.1 | Reactor vessel and accessories | 2004852
221.11 | Reactor support | 762382.4
221.12 | Outer vessel structure | 1201688.6
221.13 | Inner vessel structure | 40781
221.2 | Reactor control devices | 2114223
221.21 | Reactivity control system | 2114223
221.211 | Reactivity Control System Fabrication | 1391560
221.212 | Installation | 322663
221.213 | Control Drums Materials (Absorber) | 400000
221.214 | Control Drums Materials (Reflector)
221.3 | Non-fuel core internals | 4818221.6
221.31 | Reflector | 4170231
221.311 | Reflector (Materials: BeO) | 3200000
221.312 | Reflector (Materials: Be Metal) | 850000
221.313 | Reflector (installation | 120231
221.32 | Shield | 647990.6
221.33 | Moderator | 0
222 | Main Heat Transport System | 5908950.6
222.1 | Fluid circulation drive system | 0
222.2 | Reactor Heat Hransfer Piping System | 4890230.6
222.21 | Reactor Heat Hransfer Piping System (Mat) | 1520786
222.22 | Reactor Heat Hransfer Piping System (Fabrication) | 3341486
222.23 | Reactor Heat Hransfer Piping System (Installation) | 27958.6
222.3 | Heat Exchangers | 0
222.4 | Pressurizer System | 0
222.5 | Initial Heat Transfer Fluid Inventory | 1018720
224 | Radioactive Byproduct Processing Systems
226 | Other Reactor Plant Equipment | 456297
227 | Reactor Instrumentation and Control (I&C) | 2253208.37
228 | Reactor Plant Miscellaneous Items | 30960
23 | Energy Conversion System | 0
232 | Energy Applications | 0
232.1 | Electricity Generation Systems | 0
24 | Electrical Equipment | 73415.62
244 | Protective Systems Equipment | 1627.02
245 | Electrical Raceway Systems | 0
246 | Power and Control Cables and Wiring | 71788.6
25 | Initial Fuel Inventory | 9836580.5
254 | First Core Fuel Assembly Fabrication | 9836580.5
26 | Miscellaneous Equipment
30 | Capitalized Indirect Services Cost | 6442742.5237
31 | Factory & Field Indirect Costs | 1333020.8
317 | Field Shops | 1333020.8
33 | Startup Costs | 2407166.4
331 | Commissioning and Trial Test Runs | 2407166.4
331.3 | Initial Fuel Loading Operations | 215000
331.5 | Test Runs | 2192166.4
34 | Shipping and Transportation Costs | 1665282.8
341 | Fuel Shipping and Transportation | 1635355.8
345 | Other Shipping and Transportation Costs | 29927
35 | Engineering Services | 620313.5877
351 | Off-Site | 257261.4
352 | On-Site | 363052.1877
36 | PM/CM Services | 416958.936
361 | Off-Site
362 | On-Site | 416958.936
40 | Capitalized Training Costs | 4169765
41 | Staff Recruitment and Training | 4169765
50 | Capitalized Supplementary Costs | 16408781.6
54 | Decommissioning | 16408781.6
60 | Capitalized Financial Costs | 6160606
61 | Escalation | 6160606
70 | Annualized O&M Cost | 2456659.2
71 | O&M Staff | 2456659.2
Non-Recurrung Costs | Non-Recurrung Costs | 33779050.1383

## Design Variables
Variable | Value | Units | Description
Overall System
Thermal power | 83 | kWth | —
Electric Power | 20 | kWe
Core outer radius | 5.5 | inches | —
Reflector outer radius | 16.5 | inches | —
Fuel
Fuel mass | 145.3 | kg | UZrH
U Weight fraction | 30 | wt% | U/UZrH
U enrichment | 19.75 | wt% | High-assay low-enriched uranium (HALEU)
Pins | 36 | # | —
Reflector
Outer reflector material | BeO | — | 99% theoretical density
Elements | 124 | # | Quarter plates
Reflector plate thickness | 1 | inches | —
Reflector plate volume | 818.4 | cm3/plate | —
Mass of BeO reflector | 318 | Kg
Insert volume | 570 | cm3/plate | —
Mass of Be-metal reflector | 0.019 | MT | —
Control Elements
Control drums | 4 | # | —
Shutdown rods | 1 | # | —
Control drum elements | 124 | # | Discs
Drum disc thickness | 1 | inches | —
Drum reflector volume | 880.8 | cm3/plate | BeO 99%
Mass of drum reflector | 309 | Kg | —
Drum poison volume | 49.2 | cm3/plate | B4C
Mass of drum poison | 14 | Kg | —
Mass of rod poison | 14 | Kg | B4C
Instruments and Controls
Control cabinet | 5 |  | —
Instrument cabinet | 2 |  | —
Nuclear input/output (IO) | 9 |  | —
Non-nuclear IO | 213 |  | —
Stirling engine IO | 48 | — | These should be excluded if there no stirling engine?
TOTAL | 277
Shielding in Vessel
Stainless Steel cans | 54.2 | Kg | Stainless Steel cans of the boron carbide shielding material (SS316H)
Gamma shield material | 56.3 | Kg | Gamma shield material inside the guard vessel (of Tungsten)
Neutron shield material in the guard vessel | 39.7 | Kg | made of natural B4C powder and is located above the core (a donut around the core barrel)—
Boron Carbine shielding | 95.3 | Kg | made of natural B4C (called base shield) below the core
Radial (lead) | 2571.9 | Kg | lead
Radial (WEP) | 925.3 | Kg | made of Water Extended Polyster (WEP)
Shielding in Pit
Mass of the pit neutron shielding | 8.3 | MT | Approximated 6-in.-thick covering whole pit and made of Water-extruded poly (WEP)
Heat Transfer
Mass of coolant | 156 | Kg | —
Number of loops | 4 | # | —
Mass of PCSs | 0.86 | MT | SS316H
Subassembly Structure Masses
Reactor support frame | 1.11 | MT | —
Guard vessel | 1.587 | MT | —

## Inflation Adjustment
Year | General | Labor | Material | Equipment | Lab and Mat and Equip | Lab and Equip
1985 | 2.4641 | 3.1849 | 3.0545 | 3.8306 | 3.3566 | 3.5077
1986 | 2.4153 | 3.0852 | 3.0607 | 3.7331 | 3.293 | 3.4092
1987 | 2.3571 | 2.9916 | 2.9992 | 3.6991 | 3.23 | 3.3453
1988 | 2.2768 | 2.8748 | 2.8406 | 3.5246 | 3.08 | 3.1997
1989 | 2.1908 | 2.7813 | 2.7498 | 3.3127 | 2.9479 | 3.047
1990 | 2.1116 | 2.6589 | 2.7466 | 3.2241 | 2.8765 | 2.9415
1991 | 2.0426 | 2.554 | 2.7291 | 3.1182 | 2.8004 | 2.8361
1992 | 1.9972 | 2.4751 | 2.6817 | 2.99 | 2.7156 | 2.7325
1993 | 1.9509 | 2.3964 | 2.5547 | 2.8241 | 2.5917 | 2.6102
1994 | 1.9101 | 2.3109 | 2.4545 | 2.7417 | 2.5024 | 2.5263
1995 | 1.8708 | 2.2707 | 2.3663 | 2.6949 | 2.4439 | 2.4828
1996 | 1.8373 | 2.215 | 2.3528 | 2.6375 | 2.4018 | 2.4263
1997 | 1.8061 | 2.1583 | 2.3124 | 2.576 | 2.3489 | 2.3671
1998 | 1.786 | 2.0934 | 2.3237 | 2.5207 | 2.3126 | 2.3071
1999 | 1.7611 | 2.024 | 2.3013 | 2.5047 | 2.2767 | 2.2644
2000 | 1.7221 | 1.9301 | 2.2793 | 2.4782 | 2.2292 | 2.2042
2001 | 1.6841 | 1.8435 | 2.3007 | 2.3994 | 2.1812 | 2.1214
2002 | 1.6583 | 1.783 | 2.2814 | 2.3771 | 2.1472 | 2.08
2003 | 1.6263 | 1.7217 | 2.2333 | 2.3372 | 2.0974 | 2.0294
2004 | 1.5838 | 1.6722 | 2.0346 | 2.2508 | 1.9859 | 1.9615
2005 | 1.5356 | 1.6186 | 1.9376 | 2.163 | 1.9064 | 1.8908
2006 | 1.4896 | 1.566 | 1.8228 | 1.9965 | 1.7951 | 1.7813
2007 | 1.4503 | 1.5071 | 1.7936 | 1.8327 | 1.7111 | 1.6699
2008 | 1.4228 | 1.455 | 1.6724 | 1.7874 | 1.6383 | 1.6212
2009 | 1.4141 | 1.4394 | 1.7367 | 1.7643 | 1.6468 | 1.6018
2010 | 1.3972 | 1.424 | 1.6891 | 1.7753 | 1.6295 | 1.5996
2011 | 1.3689 | 1.409 | 1.6335 | 1.7021 | 1.5815 | 1.5555
2012 | 1.3439 | 1.387 | 1.5962 | 1.5912 | 1.5248 | 1.4891
2013 | 1.3214 | 1.3588 | 1.5699 | 1.5349 | 1.4879 | 1.4469
2014 | 1.2988 | 1.3395 | 1.532 | 1.4777 | 1.4497 | 1.4086
2015 | 1.2868 | 1.312 | 1.5385 | 1.4366 | 1.4291 | 1.3743
2016 | 1.2747 | 1.2847 | 1.536 | 1.4153 | 1.412 | 1.35
2017 | 1.2523 | 1.2535 | 1.4823 | 1.3824 | 1.3727 | 1.318
2018 | 1.2243 | 1.2201 | 1.3936 | 1.3336 | 1.3157 | 1.2768
2019 | 1.2041 | 1.1832 | 1.3937 | 1.3 | 1.2923 | 1.2416
2020 | 1.1885 | 1.1509 | 1.3736 | 1.2822 | 1.2689 | 1.2165
2021 | 1.1365 | 1.1172 | 1.0828 | 1.2259 | 1.142 | 1.1715
2022 | 1.0616 | 1.0737 | 0.96194 | 1.0847 | 1.0401 | 1.0792
2023 | 1.0242 | 1.0296 | 0.99021 | 1.0049 | 1.0082 | 1.0172
2024 | 1 | 1 | 1 | 1 | 1 | 1

## Economics Parameters
Parameter | Value
indirect to direct field-related cost | 0.06539
FTEs Per Onsite Operator (24/7) | 5
FTEs Per Offsite Operator (24/7) | 5
FTEs Per Security Staff (24/7) | 5
Hours Per FTE | 1800
Work Hours Per Shift | 10
Maintenance to Direct Cost Ratio | 0.01