## cost estimate
Account | Account Title | FOAK Estimated Cost ($2025) | NOAK Estimated Cost ($2025) | FOAK Estimated Cost std ($2025) | NOAK Estimated Cost std ($2025) | FOAK LCOE | NOAK LCOE | FOAK LCOE_std | NOAK LCOE_std
10 | Capitalized Pre-Construction Costs | 39697108 | 39697108 | 4043953 | 4043953 | 130 | 130 | 13 | 13
11 | Land Cost | 80107 | 80107 | 10984 | 10984 | 0 | 0 | 0 | 0
12 | Site Permits | 30449 | 30449 | 2918 | 2918 | 0 | 0 | 0 | 0
13 | Plant Licensing | 28670297 | 28670297 | 3512786 | 3512786 | 94 | 94 | 11 | 11
14 | Plant Permits | 5384381 | 5384381 | 931297 | 931297 | 17 | 17 | 3 | 3
15 | Plant Studies | 5531872 | 5531872 | 791230 | 791230 | 18 | 18 | 2 | 2
20 | Capitalized Direct Costs | 98332241 | 41383690 | 8934030 | 4619221 | 322 | 135 | 29 | 15
21 | Structures and Improvements | 8371043 | 2398460 | 2482756 | 446487 | 27 | 7 | 8 | 1
211 | Site Preparation/ Yard Work | 207179 | 119058 | 23250 | 13361 | 0 | 0 | 0 | 0
211.1 | Cleaning and Grubbing | 125121 | 71902 | 21234 | 12202 | 0 | 0 | 0 | 0
211.2 | Stripping Topsoil | 68141 | 39158 | 12439 | 7148 | 0 | 0 | 0 | 0
211.3 | Excavation | 13917 | 7997 | 1680 | 965 | 0 | 0 | 0 | 0
212 | Reactor Island Civil Structures | 1946452 | 1118549 | 534397 | 307097 | 6 | 3 | 1 | 1
212.1 | Reactor Building Slab Roof | 192280 | 110496 | 36813 | 21155 | 0 | 0 | 0 | 0
212.2 | Reactor Building Basement | 158011 | 90803 | 28868 | 16589 | 0 | 0 | 0 | 0
212.3 | Reactor Building Walls | 162888 | 93605 | 23695 | 13616 | 0 | 0 | 0 | 0
212.4 | Reactor Building Liner | 1339980 | 770034 | 516579 | 296858 | 4 | 2 | 1 | 0
212.5 | Reactor Building HVAC | 93290 | 53610 | 106275 | 61072 | 0 | 0 | 0 | 0
213 | Main Function Buildings | 76621 | 44031 | 5126 | 2946 | 0 | 0 | 0 | 0
213.1 | Energy conversion Building | 51685 | 29701 | 4783 | 2748 | 0 | 0 | 0 | 0
213.11 | Energy Conversion Building Slab Roof | 15579 | 8952 | 1988 | 1142 | 0 | 0 | 0 | 0
213.12 | Energy Conversion Building Basement | 12220 | 7022 | 2164 | 1243 | 0 | 0 | 0 | 0
213.13 | Energy Conversion Building Walls | 23886 | 13726 | 3981 | 2287 | 0 | 0 | 0 | 0
213.2 | Control building | 24936 | 14330 | 1680 | 965 | 0 | 0 | 0 | 0
213.21 | Control Building Slab Roof | 7921 | 4552 | 1460 | 839 | 0 | 0 | 0 | 0
213.22 | Control Building Basement | 6188 | 3556 | 1247 | 717 | 0 | 0 | 0 | 0
213.23 | Control Building Walls | 10826 | 6221 | 1422 | 817 | 0 | 0 | 0 | 0
214 | Buildings to Support Main Function | 6099479 | 1093081 | 2648524 | 468256 | 20 | 3 | 8 | 1
214.7 | Emergency and Start-up Power Systems Building | 6061123 | 1071039 | 2647918 | 467904 | 19 | 3 | 8 | 1
214.72 | Diesel Generator | 6061123 | 1071039 | 2647918 | 467904 | 19 | 3 | 8 | 1
214.8 | Auxilliary Building | 38355 | 22041 | 3897 | 2239 | 0 | 0 | 0 | 0
214.81 | Maniplator Building | 38355 | 22041 | 3897 | 2239 | 0 | 0 | 0 | 0
214.811 | Manipulator Building Slab Roof | 6726 | 3865 | 936 | 538 | 0 | 0 | 0 | 0
214.812 | ManipulatorBuilding Basement | 19092 | 10971 | 2511 | 1443 | 0 | 0 | 0 | 0
214.813 | Manipulator Building Exterior Walls | 12535 | 7203 | 2244 | 1289 | 0 | 0 | 0 | 0
215 | Supply Chain Buildings | 41310 | 23739 | 3879 | 2229 | 0 | 0 | 0 | 0
215.1 | Storage Building | 41310 | 23739 | 3879 | 2229 | 0 | 0 | 0 | 0
215.11 | Storage Building Slab Roof | 16635 | 9560 | 2433 | 1398 | 0 | 0 | 0 | 0
215.12 | Storage Building Basement | 12123 | 6966 | 1680 | 965 | 0 | 0 | 0 | 0
215.13 | Storage Building Walls | 12551 | 7212 | 1357 | 780 | 0 | 0 | 0 | 0
22 | Reactor System | 52475314 | 15917792 | 4020134 | 1352248 | 172 | 52 | 13 | 4
221 | Reactor Components | 36636652 | 8167717 | 3155743 | 837012 | 120 | 26 | 10 | 2
221.1 | Reactor Vessel and Accessories | 22220554 | 5734692 | 3611668 | 932101 | 72 | 18 | 11 | 3
221.11 | Reactor Support | 3575172 | 922682 | 719098 | 185585 | 11 | 3 | 2 | 0
221.13 | Inner Vessel Structure - stainless_steel | 18645381 | 4812009 | 3265537 | 842771 | 61 | 15 | 10 | 2
221.2 | Reactor Control Devices | 11239107 | 1871630 | 1472366 | 243896 | 36 | 6 | 4 | 0
221.21 | Reactivity Control System | 11239107 | 1871630 | 1472366 | 243896 | 36 | 6 | 4 | 0
221.211 | Reactivity Control System Fabrication | 4516927 | 720678 | 1102205 | 175857 | 14 | 2 | 3 | 0
221.212 | Installation | 1085581 | 173205 | 149238 | 23811 | 3 | 0 | 0 | 0
221.213 | Control Drums Materials (Absorber) - B4C_natural | 4096203 | 723825 | 752168 | 132913 | 13 | 2 | 2 | 0
221.214 | Control Drums Materials (Reflector) - Graphite | 475034 | 83941 | 63382 | 11200 | 1 | 0 | 0 | 0
221.215 | Control System Drive Mechanism | 1065360 | 169978 | 179225 | 28595 | 3 | 0 | 0 | 0
221.3 | Non-Fuel Core Internals | 3176990 | 561394 | 273981 | 48414 | 10 | 1 | 0 | 0
221.31 | Reflector | 1706635 | 301573 | 183775 | 32474 | 5 | 0 | 0 | 0
221.311 | Radial Reflector - Graphite | 1004525 | 177506 | 169406 | 29935 | 3 | 0 | 0 | 0
221.312 | Axial Reflector - Graphite | 702110 | 124067 | 71218 | 12584 | 2 | 0 | 0 | 0
221.32 | Shield | 576372 | 101848 | 106524 | 18823 | 1 | 0 | 0 | 0
221.322 | Out The Vessel Shield Materials - WEP | 576372 | 101848 | 106524 | 18823 | 1 | 0 | 0 | 0
221.33 | Moderator - monolith_graphite | 893982 | 157972 | 118251 | 20895 | 2 | 0 | 0 | 0
222 | Main Heat Transport System | 2743690 | 484827 | 1302959 | 230241 | 8 | 1 | 4 | 0
222.2 | Reactor Heat Transfer Piping System - HPMR | 2364808 | 417876 | 1310377 | 231552 | 7 | 1 | 4 | 0
222.3 | Heat Exchangers | 378882 | 66950 | 68163 | 12044 | 1 | 0 | 0 | 0
222.31 | Primary Heat Exchanger - SS316 | 378882 | 66950 | 68163 | 12044 | 1 | 0 | 0 | 0
223 | Safety Systems | 3793814 | 670391 | 393364 | 69510 | 12 | 2 | 1 | 0
223.2 | Reactor Cavity Cooling System (Rvacs) | 3793814 | 670391 | 393364 | 69510 | 12 | 2 | 1 | 0
223.21 | Rvacs (Cooling Vessel) | 1876199 | 331536 | 210458 | 37189 | 6 | 1 | 0 | 0
223.22 | Rvacs (Intake Vessel) | 1917614 | 338854 | 340326 | 60137 | 6 | 1 | 1 | 0
227 | Reactor Instrumentation and Control (I&C) | 9263298 | 6588165 | 1550716 | 1102887 | 30 | 21 | 5 | 3
228 | Reactor Plant Miscellaneous Items | 37858 | 6689 | 7697 | 1360 | 0 | 0 | 0 | 0
23 | Energy Conversion System | 11343241 | 8067445 | 6028052 | 4287220 | 37 | 26 | 19 | 14
232 | Energy Applications | 10171067 | 7233781 | 6101211 | 4339252 | 33 | 23 | 20 | 14
232.1 | Electricity Generation Systems | 10171067 | 7233781 | 6101211 | 4339252 | 33 | 23 | 20 | 14
236 | Common Instrumentation & Controls | 1172174 | 833664 | 231428 | 164594 | 3 | 2 | 0 | 0
24 | Electrical Equipment | 7414601 | 5273350 | 4634474 | 3296092 | 24 | 17 | 15 | 10
241 | Switchgear | 719371 | 511625 | 475790 | 338387 | 2 | 1 | 1 | 1
242 | Station Service Equipment | 407980 | 290160 | 331200 | 235553 | 1 | 0 | 1 | 0
243 | Switchboards | 124814 | 88769 | 89000 | 63297 | 0 | 0 | 0 | 0
244 | Protective Equipment | 439039 | 312249 | 205067 | 145846 | 1 | 1 | 0 | 0
245 | Electrical Structure & Wiring Container | 4012359 | 2853636 | 4447105 | 3162833 | 13 | 9 | 14 | 10
246 | Power & Control Wiring | 1711036 | 1216908 | 993625 | 706678 | 5 | 3 | 3 | 2
25 | Initial Fuel Inventory | 17286176 | 9471855 | 1750968 | 1351321 | 56 | 31 | 5 | 4
251 | First Core Mining | 4360036 | 4360036 | 661871 | 661871 | 14 | 14 | 2 | 2
252 | First Core Conversion | 335868 | 335868 | 54581 | 54581 | 1 | 1 | 0 | 0
253 | First Core Enrichment | 3098733 | 3098733 | 1333321 | 1333321 | 10 | 10 | 4 | 4
254 | First Core Fuel Assembly Fabrication - Yes | 9491536 | 1677216 | 1576616 | 278598 | 31 | 5 | 5 | 0
26 | Miscellaneous Equipment (Cranes) | 1441863 | 254786 | 286193 | 50572 | 4 | 0 | 0 | 0
30 | Capitalized Indirect Services Cost | 10564746 | 4906172 | 1141793 | 576710 | 34 | 16 | 3 | 1
31 | Factory & field indirect costs | 4720473 | 1725228 | 453327 | 262280 | 15 | 5 | 1 | 0
32 | Factory and construction supervision | 766146 | 262743 | 277222 | 69174 | 2 | 0 | 0 | 0
33 | Startup Costs | 2956438 | 1698949 | 690028 | 396532 | 9 | 5 | 2 | 1
34 | Shipping and Transportation Costs | 946521 | 543928 | 188119 | 108104 | 3 | 1 | 0 | 0
35 | Engineering Services | 681104 | 391404 | 171615 | 98620 | 2 | 1 | 0 | 0
36 | PM/CM Services | 494062 | 283918 | 94936 | 54556 | 1 | 0 | 0 | 0
40 | Capitalized training costs | 348540 | 348540 | 71174 | 71174 | 1 | 1 | 0 | 0
41 | staff recruitment and training | 348540 | 348540 | 71174 | 71174 | 1 | 1 | 0 | 0
60 | Capitalized Financial Costs | 2570726 | 1490137 | 180229 | 109691 | 8 | 4 | 0 | 0
62 | Interest | 2570726 | 1490137 | 180229 | 109691 | 8 | 4 | 0 | 0
70 | Annualized O&M Cost | 8262564 | 3232380 | 612917 | 298380 | 380 | 148 | 28 | 13
71 | O&M Staff | 1138626 | 1138626 | 160341 | 160341 | 52 | 52 | 7 | 7
711 | Operators | 7259 | 7259 | 854 | 854 | 0 | 0 | 0 | 0
712 | Remote Monitoring Technicians - Remotely Monitored | 127415 | 127415 | 32574 | 32574 | 5 | 5 | 1 | 1
713 | Security Staff | 1003951 | 1003951 | 160918 | 160918 | 46 | 46 | 7 | 7
73 | Regulatory Costs | 117599 | 117599 | 29009 | 29009 | 5 | 5 | 1 | 1
75 | Capital Plant Expenditures | 6941593 | 1938122 | 550784 | 205685 | 319 | 89 | 25 | 9
752 | Annualized Inner Vessel Structure Replacements | 3034905 | 783250 | 531531 | 137177 | 139 | 36 | 24 | 6
753 | Annualized Moderator Replacements | 366188 | 64707 | 48437 | 8559 | 16 | 2 | 2 | 0
754 | Annualized Reflector Replacements | 277788 | 49087 | 29913 | 5285 | 12 | 2 | 1 | 0
755 | Annualized Reactor Control Devices Replacements | 1829387 | 304645 | 239656 | 39698 | 84 | 14 | 11 | 1
759 | Annualized Plant Maintenance (Misc.) | 1433322 | 736432 | 229308 | 144787 | 66 | 33 | 10 | 6
759.1 | Annualized Building and Structural Maintenance (Accounts 212–215) | 244915 | 68382 | 74500 | 13362 | 11 | 3 | 3 | 0
759.2 | Annualized Main Heat Transport System Maintenance (Accounts 222.1–222.3 and 222.6) | 82310 | 14544 | 39088 | 6907 | 3 | 0 | 1 | 0
759.3 | Annualized Safety System Maintenance (Account 223) | 113814 | 20111 | 11800 | 2085 | 5 | 0 | 0 | 0
759.4 | Annualized Reactor Plant Equipment Maintenance (Accounts 221.11, 226, and 228) | 108390 | 27881 | 21603 | 5572 | 4 | 1 | 0 | 0
759.5 | Annualized Reactor I&C Maintenance (Account 227) | 277898 | 197644 | 46521 | 33086 | 12 | 9 | 2 | 1
759.6 | Annualized Energy Conversion System Maintenance (Account 23) | 340297 | 242023 | 180841 | 128616 | 15 | 11 | 8 | 5
759.7 | Annualized Electrical Equipment Maintenance (Account 24) | 222438 | 158200 | 139034 | 98882 | 10 | 7 | 6 | 4
759.8 | Annualized Miscellaneous Equipment Maintenance (Account 26) | 43255 | 7643 | 8585 | 1517 | 1 | 0 | 0 | 0
78 | Annualized Decommissioning Cost | 64744 | 38032 | 4568 | 2890 | 2 | 1 | 0 | 0
80 | Annualized Fuel Cost | 7109956 | 3909095 | 716570 | 553149 | 327 | 180 | 32 | 25
81 | Refueling Operations | 5083 | 5083 | 666 | 666 | 0 | 0 | 0 | 0
82 | Additional Nuclear Fuel | 7080673 | 3879811 | 717222 | 553521 | 326 | 178 | 33 | 25
83 | Spent Fuel Management | 24199 | 24199 | 3315 | 3315 | 1 | 1 | 0 | 0
OCC | Overnight Capital Cost | 148942637 | 86335512 | 10442145 | 6355295 | - | - | - | -
OCC per kW | Overnight Capital Cost per kW | 59104 | 34260 | 4143 | 2521 | - | - | - | -
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 131656461 | 76863657 | 10078528 | 6520699 | - | - | - | -
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 52244 | 30501 | 3999 | 2587 | - | - | - | -
TCI | Total Capital Investment | 151513363 | 87825650 | 10622375 | 6464986 | - | - | - | -
TCI per kW | Total Capital Investment per kW | 60124 | 34851 | 4215 | 2565 | - | - | - | -
AC | Annualized Cost | 15372520 | 7141476 | 933705 | 532139 | - | - | - | -
AC per MWh | Annualized Cost per MWh | 707 | 328 | 42 | 24 | - | - | - | -
LCOE | Levelized Cost Of Energy ($/MWh) | 1204 | 616 | 70 | 36 | - | - | - | -
LCOH | Levelized Cost Of Heat ($/MWth) | 388 | 196 | 22 | 11 | - | - | - | -

## Parameters
Group | Parameter | Value | Units | Description | Source
--- SETTINGS ---
Settings | Parametric Screening Mode | TRUE |  | Reduced-cost comparison mode: temperature coefficient at BOL and nearest saved EOL, shutdown margin at BOL, and non-blocking central-value constraint flags. | User Input
Settings | cross_sections_xml_location | /projects/MRP_MOUSE/openmc_data/endfb-viii.0-hdf5/cross_sections.xml |  | File path to the OpenMC cross sections XML file on HPC | User Input
Settings | plotting | N |  | Whether to generate and save geometry plots (Y = yes, N = no) | User Input
Settings | simplified_chain_thermal_xml | /projects/MRP_MOUSE/openmc_data/chain_endf_b8.0.xml |  | File path to the simplified depletion chain XML file for thermal reactors | User Input
--- MATERIALS ---
Materials | Axial Reflector | Graphite |  | Axial reflector material type — may differ from radial reflector | User Input
Materials | Common Temperature | 1000 | K | Uniform operating temperature applied to all materials in isothermal simulations | User Input
Materials | Control Drum Absorber | B4C_natural |  | Neutron absorber material in the control drums (e.g. B4C_enriched, B4C_natural) | User Input
Materials | Control Drum Reflector | Graphite |  | Reflector material in the control drums (e.g. Graphite) | User Input
Materials | Coolant | Helium |  | Primary coolant material type (e.g. NaK, Helium) | User Input
Materials | Cooling Device | heatpipe |  | Primary heat removal device type (e.g. heatpipe for HPMR) | User Input
Materials | Enrichment | 0.19985 | fraction | Uranium-235 enrichment fraction (0 to 1) | User Input
Materials | Fuel | homog_TRISO |  | Primary fuel material type (e.g. TRIGA_fuel, UO2, UN, UC, homog_TRISO) | User Input
Materials | Graphite Linear Expansion Coefficient | 4.3e-06 | 1/K | Mean linear thermal-expansion coefficient used to adjust GCMR graphite number density in density-aware temperature-coefficient cases. | User Input; IG-110 proxy from ORNL/TM-2017/705, Table 2.2, page 3
Materials | HX Material | SS316 |  | Heat exchanger structural material (e.g. SS316) | User Input
Materials | Moderator | monolith_graphite |  | Neutron moderator material type (e.g. ZrH, Graphite, monolith_graphite) | User Input
Materials | Radial Reflector | Graphite |  | Radial reflector material type (e.g. Graphite, BeO) | User Input
Materials | TRISO Fueled | Yes |  | Whether the reactor uses TRISO fuel particles (Yes or No) | User Input
Materials | reactor type | HPMR |  | Reactor type identifier: LTMR (liquid metal thermal), GCMR (gas-cooled), or HPMR (heat pipe) | User Input
--- GEOMETRY ---
Geometry | Active Height | 249.9565 | cm | Axial height of the active fuel region | User Input
Geometry | Assembly FTF | 31.991 | cm | Assembly flat-to-flat distance (distance between opposite parallel faces of the hexagonal assembly). | User Input or Calculated
Geometry | Axial Reflector Thickness | 50 | cm | Thickness of each axial neutron reflector (top and bottom) | User Input
Geometry | Core Radius | 124.9783 | cm | Total core radius including the radial reflector | User Input or Calculated
Geometry | Fuel Assemblies Count | 18 |  | Total number of fuel assemblies in the core (HPMR) | Calculated
Geometry | Fuel Pin Count | 1296 |  | Total number of fuel pins (or fuel elements) in the entire core | Calculated
Geometry | Fuel Pin Count per Assembly | 72 |  | Number of fuel pins per hexagonal assembly (HPMR) | Calculated
Geometry | Fuel Pin Materials | ['homog_TRISO', 'Helium'] |  | Ordered list of materials for each fuel pin region from innermost to outermost | User Input
Geometry | Fuel Pin Radii | [1.0, 1.05] | cm | Ordered list of radii defining fuel pin region boundaries from innermost to outermost | User Input
Geometry | Heat Pipe Materials | ['heatpipe', 'Helium'] |  | Ordered list of materials for each heat pipe region (HPMR) | User Input
Geometry | Heat Pipe Radii | [1.1, 1.15] | cm | Ordered list of radii defining heat pipe region boundaries (HPMR) | User Input
Geometry | Lattice Pitch | 3.4 | cm | Center-to-center distance between adjacent lattice positions | User Input
Geometry | Number of Heatpipes | 342 |  | Total number of heat pipes in the entire core (HPMR) | Calculated
Geometry | Number of Heatpipes per Assembly | 19 |  | Number of heat pipes per hexagonal assembly (HPMR) | Calculated
Geometry | Number of Rings per Assembly | 6 |  | Number of pin rings along the side of the hexagonal assembly (LTMR/HPMR) | User Input
Geometry | Number of Rings per Core | 3 |  | Number of assembly rings along the side of the hexagonal core (HPMR) | User Input
Geometry | Radial Reflector Thickness | 50 | cm | Thickness of the radial neutron reflector surrounding the active core | User Input
Geometry | hexagonal Core Edge Length | 86.5774 | cm | Edge length of the hexagonal core (HPMR) | Calculated
--- CONTROL DRUMS ---
Control Drums | All Drums Area | 15079.6447 | cm² | Total cross-sectional area of all control drums | Calculated
Control Drums | All Drums Volume | 3769255.7525 | cm³ | Total volume of all control drums combined | Calculated
Control Drums | Control Drum Absorber Mass | 308.702 | kg | Total mass of absorber material in all control drums | Calculated
Control Drums | Control Drum Reflector Mass | 5834.8079 | kg | Total mass of reflector material in all control drums | Calculated
Control Drums | Control Drums Mass | 6143.51 | kg | Total combined mass of all control drums (absorber + reflector) | Calculated
Control Drums | Drum Absorber Thickness | 1 | cm | Thickness of the absorber arc section within each control drum | User Input
Control Drums | Drum Count | 12 |  | Total number of control drums in the core; explicit and validated against the GCMR lattice. | User Input or Calculated
Control Drums | Drum Height | 249.9565 | cm | Height of the control drums (typically active height + 2x axial reflector thickness) | User Input
Control Drums | Drum Radius | 20 | cm | Outer radius of each control drum. If not specified, it is automatically set to the largest allowable value that avoids drum overlap. | User Input
Control Drums | Drum Tube Radius | 20.2222 | cm | Outer radius of the control drum tube. It is explicit and validated for the GCMR example and may be calculated for other models. | User Input or Calculated
--- CORE DESIGN ---
Core Design | Axial Reflector Mass | 7851.2509 | kg | Total mass of both axial reflectors (top and bottom combined) | Calculated
Core Design | Moderator Mass | 5295.8353 | kg | Total mass of the neutron moderator material in the core | Calculated
Core Design | Moderator Total Area | 12998.1748 | cm² | Total cross-sectional area occupied by moderator material in the core | Calculated
Core Design | Radial Reflector Mass | 12062.8558 | kg | Total mass of the radial neutron reflector | Calculated
--- OVERALL SYSTEM ---
Overall System | Heat Flux | 0.032754 | MW/m² | Calculated average fuel surface heat flux at full power | Calculated
Overall System | Heat Flux Criteria | 0.9 | MW/m² | Maximum allowable fuel surface heat flux (design constraint) | User Input
Overall System | Power MWe | 2.52 | MWe | Reactor net electric power output (thermal power × thermal efficiency) | Calculated
Overall System | Power MWt | 7 | MWt | Reactor thermal power output | User Input
Overall System | Thermal Efficiency | 0.36 | fraction | Net thermal-to-electric conversion efficiency of the power conversion system | User Input
Overall System | Time Steps | [864.0, 85536.0, 259200.0, 518400.0, 1728000.0, 6048000.0, 22896000.0, 31536000.0, 31536000.0, 31536000.0, 63072000.0, 63072000.0] | s | User-specified depletion step durations used by the integrator | User Input
--- OPENMC SETTINGS ---
OpenMC Settings | Cold Shutdown Temperature | 300 | K | Temperature used for the shutdown-state (ARI) keff calculation during shutdown margin evaluation. | User Input
OpenMC Settings | Depletion Integrator | predictor |  | Requested depletion integration method: predictor or cecm. | User Input
OpenMC Settings | Depletion Integrator Used | predictor |  | Depletion integration method actually used by the calculation. | Calculated
OpenMC Settings | Isothermal Temperature Coefficients | TRUE |  | Whether isothermal temperature reactivity coefficients were calculated | User Input
OpenMC Settings | Maximum Temperature Coefficient | -1 | pcm/K | Maximum allowed central-value temperature coefficient at both BOL and EOL for the parametric-screening pass/fail flag. | User Input
OpenMC Settings | Minimum Shutdown Margin | 1000 | pcm | Central-value BOL shutdown-margin threshold used for reporting the parametric-screening pass/fail flag. | User Input
OpenMC Settings | Shutdown Margin Calc | TRUE |  | Whether shutdown margin is calculated. When True, the shutdown-state keff is evaluated with the absorber facing the core (ARI) at Cold Shutdown Temperature, and shutdown margin metrics are reported from ((1 - k_s) / k_s). | User Input
OpenMC Settings | Temperature Coefficient Particles Per Batch | 4000 | particles/batch | OpenMC particle histories per batch for each parametric-screening temperature-coefficient static calculation. | User Input
OpenMC Settings | Temperature Perturbation | 100 | K | Temperature increase applied for isothermal temperature coefficient calculation | User Input
--- PHYSICS RESULTS ---
Physics Results | BOL Axial Non-Leakage Probability | 0.97783 | fraction | Beginning-of-life axial non-leakage probability from the 2D-to-3D buckling correction model. | Calculated
Physics Results | BOL Total Non-Leakage Probability | 0.88909 | fraction | Beginning-of-life total non-leakage probability from the axial-plus-radial buckling model. Returns NaN when Core Radius is not available. | Calculated
Physics Results | Depletion Time Steps | [0.0, 0.01, 1.0, 4.0, 10.0, 30.0, 100.0, 365.0, 730.0, 1095.0, 1460.0, 2190.0, 2920.0] | days | Calculated cumulative depletion times corresponding to the reported keff values and used as the x-axis in keff_comparison_vs_Time.png. | Calculated
Physics Results | Estimated Axial Leakage (%) | 2.217 | % | Estimated beginning-of-life axial neutron leakage percentage from the axial buckling correction model, computed as 100 × (1 - axial non-leakage probability). | Calculated
Physics Results | Estimated Total Leakage (%) | 11.0906 | % | Estimated beginning-of-life total neutron leakage percentage from the axial-plus-radial buckling model, computed as 100 × (1 - total non-leakage probability). Returns NaN when Core Radius is not available. | Calculated
Physics Results | Fuel Lifetime | 1002 | days | Estimated fuel cycle length — time for the 3D-corrected keff to fall to 1.0 | Calculated
Physics Results | Fuel Lifetime Extrapolated | FALSE |  | True when fuel lifetime was extrapolated beyond the simulated depletion schedule from the final two corrected keff points. | Calculated
Physics Results | Fuel Lifetime Status | Interpolated k=1 crossing |  | Whether fuel lifetime came from an interpolated k=1 crossing, BOL-subcritical result, terminal extrapolation, or simulated endpoint lower bound. | Calculated
Physics Results | Fuel Tail Waste Mass | 21864.8749 | kg | Mass of depleted uranium tails produced during the enrichment process | Calculated
Physics Results | Lifecycle Evaluation Times (BOL) | 0 | days | Actual saved-state times used for lifecycle safety evaluations. Screening mode reports BOL and nearest-saved EOL; detailed mode reports BOL, MOL, and interpolated EOL. — beginning of life | Calculated
Physics Results | Lifecycle Evaluation Times (EOL) | 1095 | days | Actual saved-state times used for lifecycle safety evaluations. Screening mode reports BOL and nearest-saved EOL; detailed mode reports BOL, MOL, and interpolated EOL. — end of life | Calculated
Physics Results | Mass U235 | 103226.6186 | g | Initial mass of U-235 in the fresh fuel load | Calculated
Physics Results | Mass U238 | 418581.0308 | g | Initial mass of U-238 in the fresh fuel load | Calculated
Physics Results | Max Peaking Factor | 2.3379 | unitless | Maximum pin peaking factor among saved depletion states at or before the calculated end of operating life | Calculated
Physics Results | Max Peaking Factors per Step | [2.1926353376929533, 2.1764437199932303, 2.247130154504472, 2.2197661202582126, 2.205982899319515, 2.2469726135552177, 2.234393439916347, 2.276615289855844, 2.33789322798978] | unitless | List of the maximum pin peaking factor at each saved depletion state at or before EOL, in step order | Calculated
Physics Results | Maximum Shutdown Margin 3D (2D corrected) | 443.7116 | pcm | Maximum shutdown margin among the BOL, MOL, and EOL evaluations after correcting shutdown-state keff from 2D to 3D using the axial leakage approximation. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) | 443.7116 | pcm | Minimum shutdown margin among the BOL, MOL, and EOL evaluations after correcting shutdown-state keff from 2D to 3D using the axial leakage approximation. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) Point | BOL |  | Lifecycle point, BOL, MOL, or EOL, at which the minimum axial-leakage-corrected shutdown margin occurs. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) Uncertainty | 399.9952 | pcm | One standard deviation OpenMC statistical uncertainty associated with the reported minimum axial-leakage-corrected shutdown margin. Axial leakage model uncertainty is excluded. | Calculated
Physics Results | Natural Uranium Mass | 22386.6825 | kg | Mass of natural uranium feed required to produce the enriched fuel | Calculated
Physics Results | Parametric Screening Pass | FALSE |  | Combined shutdown-margin and temperature-coefficient screening result. Reporting only; all engineering and cost calculations still run. | Calculated
Physics Results | Region ID with Max Peaking Factor | 881 | unitless | Region ID with the highest peaking factor among saved depletion states at or before EOL; for LTMR this is typically a pin/distribcell ID, while for GCMR it is a mesh-region index | Calculated
Physics Results | SWU | 21726.0485 | kg-SWU | Separative work units required to produce the enriched fuel | Calculated
Physics Results | Shutdown Margin 3D (2D corrected) Lifecycle (BOL) | 443.7116 | pcm | Subcritical margin relative to criticality at the configured lifecycle points using cold shutdown keff corrected from 2D to 3D. Screening mode reports BOL only. — beginning of life | Calculated
Physics Results | Shutdown Margin 3D (2D corrected) Lifecycle Uncertainty (BOL) | 399.9952 | pcm | One standard deviation OpenMC statistical uncertainty for the reported axial-leakage-corrected shutdown margin evaluations. Axial leakage model uncertainty is excluded. — beginning of life | Calculated
Physics Results | Shutdown Margin Constraint Pass | FALSE |  | Central-value BOL shutdown margin satisfies the screening threshold. Reporting only; it does not stop the run. | Calculated
Physics Results | Step with Max Peaking Factor | 9 | unitless | Saved depletion step at or before EOL at which the maximum peaking factor occurs | Calculated
Physics Results | Temp Coeff 3D (2D corrected) | -5.6655 | pcm/K | Most limiting, numerically largest isothermal temperature coefficient among the BOL, MOL, and EOL evaluations, corrected from 2D to 3D using axial neutron leakage correction. Negative values confirm self-stabilizing behavior. Use this value for safety analysis. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle (BOL) | -5.6655 | pcm/K | Isothermal temperature coefficient evaluated at the configured lifecycle points and corrected from 2D to 3D using the axial leakage approximation. — beginning of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle (EOL) | -7.2142 | pcm/K | Isothermal temperature coefficient evaluated at the configured lifecycle points and corrected from 2D to 3D using the axial leakage approximation. — end of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle Uncertainty (BOL) | 2.2091 | pcm/K | One standard deviation OpenMC statistical uncertainty for the reported axial-leakage-corrected lifecycle temperature coefficient evaluations. Axial leakage model uncertainty is excluded. — beginning of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle Uncertainty (EOL) | 2.266 | pcm/K | One standard deviation OpenMC statistical uncertainty for the reported axial-leakage-corrected lifecycle temperature coefficient evaluations. Axial leakage model uncertainty is excluded. — end of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Limiting Point | BOL |  | Lifecycle point, BOL, MOL, or EOL, at which the limiting axial-leakage-corrected isothermal temperature coefficient occurs. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Uncertainty | 2.2091 | pcm/K | One standard deviation OpenMC statistical uncertainty associated with the reported limiting axial-leakage-corrected temperature coefficient. Axial leakage model uncertainty is excluded. | Calculated
Physics Results | Temperature Coefficient Constraint Pass | TRUE |  | Central-value BOL and EOL temperature coefficients satisfy the screening threshold. Reporting only; it does not stop the run. | Calculated
Physics Results | Uranium Mass | 521.8076 | kg | Total initial uranium mass in the fresh fuel load (U-235 + U-238) | Calculated
Physics Results | keff 3D (2D corrected) | [1.0502032742860852, 1.0460317261166505, 1.045502349174007, 1.0463546805982273, 1.0391101294583396, 1.046110307153777, 1.0404623980500913, 1.0320275876340144, 1.016203852694516, 0.9944772338649129, 0.9780457046955062, 0.9496905987999552, 0.9246942690793997] |  | keff at each burnup step for the operating configuration (ARO), corrected from 2D to 3D using axial leakage correction and evaluated at Common Temperature. | Calculated
--- PRIMARY LOOP & BALANCE OF PLANT ---
Primary Loop & Balance of Plant | BoP Count | 2 |  | Number of Balance of Plant (power conversion) systems | User Input
Primary Loop & Balance of Plant | BoP Power kWe | 1260 | kWe | Electric power handled by each BoP system | Calculated
Primary Loop & Balance of Plant | BoP per loop load fraction | 0.5 | fraction | Fraction of total electric load handled by each BoP system | User Input
Primary Loop & Balance of Plant | Primary HX Mass | 1450.6623 | kg | Calculated mass of the primary heat exchanger | Calculated
Primary Loop & Balance of Plant | Primary Loop Count | 2 |  | Number of primary coolant loops | User Input
Primary Loop & Balance of Plant | Primary Loop Inlet Temperature | 923.15 | K | Primary coolant temperature at the core inlet | User Input
Primary Loop & Balance of Plant | Primary Loop Outlet Temperature | 923.15 | K | Primary coolant temperature at the core outlet | User Input
Primary Loop & Balance of Plant | Primary Loop Purification | TRUE |  | Whether primary coolant purification is used (reduces coolant replacement frequency) | User Input
Primary Loop & Balance of Plant | Secondary HX Mass | 0 | kg | Mass of the secondary heat exchanger (0 if none) | User Input
Primary Loop & Balance of Plant | Secondary Loop Inlet Temperature | 573.15 | K | Secondary loop coolant temperature at the heat exchanger inlet | User Input
Primary Loop & Balance of Plant | Secondary Loop Outlet Temperature | 903.15 | K | Secondary loop coolant temperature at the heat exchanger outlet | User Input
--- SHIELDING ---
Shielding | In Vessel Shield Inner Radius | 124.9783 | cm | Inner radius of the in-vessel radiation shield (equal to core radius) | User Input
Shielding | In Vessel Shield Mass | 0 | kg | Total mass of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Material | B4C_natural |  | Material of the in-vessel radiation shield | User Input
Shielding | In Vessel Shield Outer Radius | 124.9783 | cm | Outer radius of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Thickness | 0 | cm | Thickness of the in-vessel radiation shield (0 if none) | User Input
Shielding | Out Of Vessel Shield Effective Density Factor | 0.5 | fraction | Effective density factor for the out-of-vessel shield — accounts for partial fill (e.g. 0.5 = 50% fill) | User Input
Shielding | Out Of Vessel Shield Mass | 34359.671 | kg | Total mass of the out-of-vessel radiation shield | Calculated
Shielding | Out Of Vessel Shield Material | WEP |  | Material of the out-of-vessel radiation shield | User Input
Shielding | Out Of Vessel Shield Thickness | 90 | cm | Thickness of the out-of-vessel radiation shield | User Input
Shielding | Outer Shield Inner Radius | 137.9783 | cm | Inner radius of the out-of-vessel shield | Calculated
Shielding | Outer Shield Outer Radius | 227.9783 | cm | Outer radius of the out-of-vessel shield (outermost boundary of the shielded assembly) | Calculated
--- VESSELS ---
Vessels | Cooling Vessel Mass | 1643.9697 | kg | Total mass of the cooling vessel | Calculated
Vessels | Cooling Vessel Material | stainless_steel |  | Structural material of the cooling vessel | User Input
Vessels | Cooling Vessel Radius | 131.9783 | cm | Outer radius of the cooling vessel | Calculated
Vessels | Cooling Vessel Thickness | 0.5 | cm | Wall thickness of the cooling vessel | User Input
Vessels | Gap Between Cooling Vessel And Intake Vessel | 5 | cm | Radial gap between the cooling vessel and intake vessel | User Input
Vessels | Gap Between Guard Vessel And Cooling Vessel | 5 | cm | Radial gap between the guard vessel and cooling vessel | User Input
Vessels | Gap Between Vessel And Guard Vessel | 0 | cm | Radial gap between the reactor vessel and guard vessel | User Input
Vessels | Guard Vessel Mass | 0 | kg | Total mass of the guard vessel | Calculated
Vessels | Guard Vessel Material | low_alloy_steel |  | Structural material of the guard vessel | User Input
Vessels | Guard Vessel Radius | 126.9783 | cm | Outer radius of the guard vessel | Calculated
Vessels | Guard Vessel Thickness | 0 | cm | Wall thickness of the guard vessel (0 if none) | User Input
Vessels | Intake Vessel Mass | 1729.5938 | kg | Total mass of the intake vessel | Calculated
Vessels | Intake Vessel Material | stainless_steel |  | Structural material of the intake vessel | User Input
Vessels | Intake Vessel Radius | 137.4783 | cm | Outer radius of the intake vessel | Calculated
Vessels | Intake Vessel Thickness | 0.5 | cm | Wall thickness of the intake vessel | User Input
Vessels | Total Vessels Mass | 9554.4298 | kg | Combined mass of all vessel components (pressure vessel, guard, cooling, intake) | Calculated
Vessels | Vessel Bottom Depth | 32.129 | cm | Depth of the vessel bottom head (ellipsoidal) | User Input
Vessels | Vessel Height | 417.1085 | cm | Total height of the reactor pressure vessel | Calculated
Vessels | Vessel Lower Plenum Height | 20 | cm | Height of the lower plenum region below the active core | User Input
Vessels | Vessel Mass | 6180.8664 | kg | Total mass of the reactor pressure vessel | Calculated
Vessels | Vessel Material | stainless_steel |  | Structural material of the reactor pressure vessel | User Input
Vessels | Vessel Radius | 124.9783 | cm | Inner radius of the reactor pressure vessel (or core barrel) | User Input
Vessels | Vessel Thickness | 2 | cm | Wall thickness of the reactor pressure vessel | User Input
Vessels | Vessel Upper Gas Gap | 0 | cm | Height of the upper gas gap above the upper plenum (0 if none) | User Input
Vessels | Vessel Upper Plenum Height | 47.152 | cm | Height of the upper plenum region above the active core | User Input
Vessels | Vessels Total Height | 461.7375 | cm | Total height of the complete vessel assembly | Calculated
Vessels | Vessels Total Radius | 137.9783 | cm | Total outer radius of the complete vessel assembly | Calculated
--- OPERATION ---
Operation | A75: Inner Vessel Structure Replacement Period (cycles) | 3 | cycles | Number of fuel cycles between scheduled inner vessel structure replacements | User Input
Operation | A75: Moderator Booster Replacement Period (cycles) | 1 | cycles | Number of complete fuel cycles between moderator booster replacements | User Input
Operation | A75: Outer Vessel Structure Replacement Period (years) | 20 | years | Service period in years between scheduled outer vessel structure replacements | User Input
Operation | A75: Reactor Control Devices Replacement Period (cycles) | 3 | cycles | Number of fuel cycles between scheduled reactor control device replacements | User Input
Operation | A75: Reflector Replacement Period (cycles) | 3 | cycles | Number of fuel cycles between scheduled reflector replacements | User Input
Operation | A78: CAPEX to Decommissioning Cost Ratio | 0.15 | fraction | Ratio of total decommissioning cost to total capital cost (typical range: 9%–15%) | User Input
Operation | Annual Electricity Production | 21715.344 | MWh/year | Total annual electricity production at the calculated capacity factor | Calculated
Operation | Capacity Factor | 0.9837 | fraction | Annual plant capacity factor — fraction of the year the plant operates at full power | Calculated
Operation | Emergency Shutdowns Per Year | 0.2 | events/year | Expected number of unplanned emergency shutdowns per year | User Input
Operation | Levelization Period | 60 | years | Plant lifetime used for LCOE levelization (economic analysis period) | User Input
Operation | Maintenance to Direct Cost Ratio | 0.03 | fraction | Ratio of annual non-replacement maintenance cost to total direct capital cost | User Input
Operation | Number of On-Site Operators per Shift | 2 |  | Number of concurrent on-site operators assigned per shift | User Input
Operation | Onsite Coolant Inventory | 0 | kg | Total mass of coolant stored on site (fresh + used tanks) | User Input
Operation | Operation Mode | Remotely Monitored |  | Reactor operation mode: Remotely Monitored, On-Site Staffed, or On-Site Staffed and Remotely Monitored | User Input
Operation | Reactors Monitored Per Operator | 10 |  | Number of reactors that can be monitored by a single operator | User Input
Operation | Refueling Period | 7 | days | Duration of the scheduled refueling outage | User Input
Operation | Replacement Coolant Inventory | 0 | kg | Mass of coolant replaced per refueling cycle | User Input
Operation | Security Staff Per Shift | 1 |  | Number of security personnel required per shift | User Input
Operation | Startup Duration after Emergency Shutdown | 14 | days | Duration of the startup sequence following an emergency shutdown | User Input
Operation | Startup Duration after Refueling | 2 | days | Duration of the startup sequence following a refueling outage | User Input
--- ECONOMIC PARAMETERS ---
Economic Parameters | Annual Return | 0.0475 | fraction | Annual return rate assumed for the decommissioning reserve fund | User Input
Economic Parameters | Assumed Number Of Units For Onsite Learning | 200 |  | Number of units assumed for onsite learning (typically 2 × NOAK Unit Number) | Calculated
Economic Parameters | Construction Duration | 12 | months | Duration of plant construction used for financing cost calculation | User Input
Economic Parameters | Control Building Basement Volume | 5.9448 | m³ | Volume of concrete in the control building basement | User Input
Economic Parameters | Control Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the control building exterior walls | User Input
Economic Parameters | Control Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the control building slab roof | User Input
Economic Parameters | Cost Sampling Seed | 12345 |  | Fixed NumPy random seed used to make cost-uncertainty sampling reproducible across reactor comparisons. | User Input
Economic Parameters | Debt To Equity Ratio | 1 | fraction | Ratio of debt financing to equity financing for the project | User Input
Economic Parameters | Discount Rate | 0.07 | fraction | Annual discount rate (WACC) used for LCOE levelization and cost annualization | User Input
Economic Parameters | Emergency Building Basement Volume | 0 | m³ | Volume of concrete in the emergency building basement (0 if none) | User Input
Economic Parameters | Emergency Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the emergency building exterior walls (0 if none) | User Input
Economic Parameters | Emergency Building Slab Roof Volume | 0 | m³ | Volume of concrete in the emergency building slab roof (0 if none) | User Input
Economic Parameters | Escalation Year | 2025 | year | Reference year to which all costs are escalated for consistent comparison | User Input
Economic Parameters | Excavation Volume | 412.605 | m³ | Volume of earth to be excavated for plant construction | User Input
Economic Parameters | FTEs Per Offsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per offsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per onsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator Per Year | 0.019444 | FTE/operator/year | Total FTE-years per operator per year including all activities | Calculated
Economic Parameters | FTEs Per Operator Per Year Per Refueling | 0.013611 | FTE/operator/year | Fraction of an FTE spent per operator per year on refueling-related activities | User Input
Economic Parameters | FTEs Per Security Staff (24/7) | 5 | FTE/staff | Full-time equivalents needed per security staff position to maintain 24/7 coverage | User Input
Economic Parameters | Hours Per FTE | 1800 | hours/year | Annual working hours per full-time equivalent employee | User Input
Economic Parameters | Integrated Heat Exchanger Building Basement Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building basement (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building exterior walls (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Slab Roof Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building slab roof (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Superstructure Area | 0 | m² | Floor area of the integrated heat exchanger building superstructure (0 if none) | User Input
Economic Parameters | Interest Rate | 0.07 | fraction | Annual cost of debt used to calculate interest during construction (Account 62) | User Input
Economic Parameters | Land Area | 18 | acres | Total land area required for the plant site | User Input
Economic Parameters | Manipulator Building Basement Volume | 17.8374 | m³ | Volume of concrete in the manipulator building basement | User Input
Economic Parameters | Manipulator Building Exterior Walls Volume | 15.9195 | m³ | Volume of concrete in the manipulator building exterior walls | User Input
Economic Parameters | Manipulator Building Slab Roof Volume | 4.7566 | m³ | Volume of concrete in the manipulator building slab roof | User Input
Economic Parameters | NOAK Unit Number | 100 |  | Nth-of-a-kind unit number used to calculate the learning curve cost multiplier | User Input
Economic Parameters | Number of Samples | 20 |  | Number of Monte Carlo samples used for cost uncertainty quantification | User Input
Economic Parameters | Radwaste Building Basement Volume | 0 | m³ | Volume of concrete in the radioactive waste building basement (0 if none) | User Input
Economic Parameters | Radwaste Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the radioactive waste building exterior walls (0 if none) | User Input
Economic Parameters | Radwaste Building Slab Roof Volume | 0 | m³ | Volume of concrete in the radioactive waste building slab roof (0 if none) | User Input
Economic Parameters | Reactor Building Basement Volume | 95.0976 | m³ | Volume of concrete in the reactor building basement | User Input
Economic Parameters | Reactor Building Exterior Walls Volume | 129.9564 | m³ | Volume of concrete in the reactor building exterior walls | User Input
Economic Parameters | Reactor Building Slab Roof Volume | 95.0976 | m³ | Volume of concrete in the reactor building slab roof | User Input
Economic Parameters | Reactor Building Superstructure Area | 77 | m² | Floor area of the reactor building superstructure | User Input
Economic Parameters | Refueling Building Basement Volume | 0 | m³ | Volume of concrete in the refueling building basement (0 if none) | User Input
Economic Parameters | Refueling Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the refueling building exterior walls (0 if none) | User Input
Economic Parameters | Refueling Building Slab Roof Volume | 0 | m³ | Volume of concrete in the refueling building slab roof (0 if none) | User Input
Economic Parameters | Spent Fuel Building Basement Volume | 0 | m³ | Volume of concrete in the spent fuel building basement (0 if none) | User Input
Economic Parameters | Spent Fuel Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the spent fuel building exterior walls (0 if none) | User Input
Economic Parameters | Spent Fuel Building Slab Roof Volume | 0 | m³ | Volume of concrete in the spent fuel building slab roof (0 if none) | User Input
Economic Parameters | Storage Building Basement Volume | 11.76 | m³ | Volume of concrete in the storage building basement | User Input
Economic Parameters | Storage Building Exterior Walls Volume | 15.768 | m³ | Volume of concrete in the storage building exterior walls | User Input
Economic Parameters | Storage Building Slab Roof Volume | 11.76 | m³ | Volume of concrete in the storage building slab roof (houses operational spares) | User Input
Economic Parameters | Turbine Building Basement Volume | 5.9448 | m³ | Volume of concrete in the turbine building basement | User Input
Economic Parameters | Turbine Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the turbine building exterior walls | User Input
Economic Parameters | Turbine Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the turbine building slab roof | User Input
Economic Parameters | Work Hours Per Shift | 10 | hours | Duration of each work shift | User Input
Economic Parameters | indirect to direct field-related cost | 0.06539 | fraction | Ratio of indirect field (site) costs to total direct field costs — covers site supervision, temporary facilities, and other indirect site activities | User Input
--- LEARNING RATES ---
Learning Rates | Factory Be | 0.41505 | fraction | Learning rate for factory-manufactured beryllium components | User Input
Learning Rates | Factory Be Cost Multiplier | 0.028363 | fraction | NOAK cost multiplier for beryllium components based on Wright's Law | Calculated
Learning Rates | Factory BeO | 0.39915 | fraction | Learning rate for factory-manufactured beryllium oxide components | User Input
Learning Rates | Factory BeO Cost Multiplier | 0.033897 | fraction | NOAK cost multiplier for beryllium oxide components based on Wright's Law | Calculated
Learning Rates | Factory Drums | 0.24138 | fraction | Learning rate for factory-manufactured control drum components | User Input
Learning Rates | Factory Drums Cost Multiplier | 0.15955 | fraction | NOAK cost multiplier for factory-built control drums based on Wright's Law | Calculated
Learning Rates | Factory Other | 0.22963 | fraction | Learning rate for other factory-manufactured components | User Input
Learning Rates | Factory Other Cost Multiplier | 0.17671 | fraction | NOAK cost multiplier for other factory-built components based on Wright's Law | Calculated
Learning Rates | Factory Primary Structure | 0.18443 | fraction | Learning rate for factory-manufactured primary structural components | User Input
Learning Rates | Factory Primary Structure Cost Multiplier | 0.25808 | fraction | NOAK cost multiplier for factory-built primary structure based on Wright's Law | Calculated
Learning Rates | Licensing Learning | 0 | fraction | Learning rate for licensing costs per doubling of cumulative units produced | User Input
Learning Rates | Licensing Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for licensing costs based on Wright's Law | Calculated
Learning Rates | No Learning | 0 | fraction | Learning rate for components with no learning benefit (fixed costs, rate = 0) | User Input
Learning Rates | No Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for components with no learning (always 1.0) | Calculated
Learning Rates | Non-nuclear off-the-shelf | 0.05 | fraction | Learning rate for non-nuclear commercial off-the-shelf components | User Input
Learning Rates | Non-nuclear off-the-shelf Cost Multiplier | 0.71121 | fraction | NOAK cost multiplier for non-nuclear commercial components based on Wright's Law | Calculated
Learning Rates | Onsite Learning | 0.08 | fraction | Learning rate for onsite construction and installation activities | User Input
Learning Rates | Onsite Learning Cost Multiplier | 0.57466 | fraction | NOAK cost multiplier for onsite construction activities based on Wright's Law | Calculated
--- DEBUG / INTERMEDIATE VALUES ---
Debug / Intermediate Values | EOL Snapshot Depletion Index | 9 |  | Saved depletion index nearest the estimated end-of-life time and used for the screening EOL temperature-coefficient calculation. | Calculated
Debug / Intermediate Values | Lifecycle Target Times (BOL) | 0 | days | Target lifecycle times before selecting saved depletion compositions. Screening mode reports BOL and estimated EOL; detailed mode also reports half-life. — beginning of life | Calculated
Debug / Intermediate Values | Lifecycle Target Times (EOL) | 1002.2194 | days | Target lifecycle times before selecting saved depletion compositions. Screening mode reports BOL and estimated EOL; detailed mode also reports half-life. — end of life | Calculated
Debug / Intermediate Values | Temperature Coefficient Base Seeds | [104729, 2104732] |  | Independent OpenMC random seeds used for the base-temperature lifecycle snapshots. | Calculated
Debug / Intermediate Values | Temperature Coefficient High Seeds | [15485863, 17485896] |  | Independent OpenMC random seeds used for the elevated-temperature lifecycle snapshots. | Calculated
Debug / Intermediate Values | Temperature Coefficient Particles | [4000, 4000] | particles per batch | Particle counts used for each unique depletion index required by the BOL, MOL, and EOL temperature-coefficient snapshot pairs. | Calculated
Debug / Intermediate Values | Temperature Coefficient Static Depletion Indices | [0, 9] |  | Unique operating depletion indices used for the BOL, MOL, and EOL temperature-coefficient snapshot pairs. | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARI (BOL) | 0.99558 |  | keff at BOL, MOL, and EOL for the cold shutdown configuration, corrected from 2D to 3D using the axial leakage approximation. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARI Uncertainty (BOL) | 0.003965 |  | One standard deviation OpenMC statistical uncertainty for cold shutdown axial-leakage-corrected keff at BOL, MOL, and EOL. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (first) | 1.0502 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — first reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (last) | 0.92469 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — last reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (min) | 0.92469 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (max) | 1.0502 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (first) | 0.003154 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — first reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (last) | 0.003074 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — last reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (min) | 0.003013 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (max) | 0.003752 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (first) | 0.003154 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — first reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (last) | 0.003074 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — last reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (min) | 0.003013 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (max) | 0.003752 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp (BOL) | 1.0518 |  | Axial-leakage-corrected keff from the dedicated nominal-temperature ARO static calculations used to evaluate the temperature coefficient at BOL, MOL, and EOL. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp (EOL) | 0.99531 |  | Axial-leakage-corrected keff from the dedicated nominal-temperature ARO static calculations used to evaluate the temperature coefficient at BOL, MOL, and EOL. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp Uncertainty (BOL) | 0.001803 |  | One standard deviation OpenMC statistical uncertainty for the dedicated nominal-temperature axial-leakage-corrected keff values used in the temperature coefficient calculations. Axial leakage model uncertainty is excluded. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp Uncertainty (EOL) | 0.001478 |  | One standard deviation OpenMC statistical uncertainty for the dedicated nominal-temperature axial-leakage-corrected keff values used in the temperature coefficient calculations. Axial leakage model uncertainty is excluded. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp (BOL) | 1.0456 |  | keff at BOL, MOL, and EOL at elevated temperature corrected to 3D — used to calculate temperature coefficient — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp (EOL) | 0.98821 |  | keff at BOL, MOL, and EOL at elevated temperature corrected to 3D — used to calculate temperature coefficient — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp Uncertainty (BOL) | 0.001631 |  | One standard deviation OpenMC statistical uncertainty for elevated-temperature axial-leakage-corrected keff at BOL, MOL, and EOL. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp Uncertainty (EOL) | 0.001666 |  | One standard deviation OpenMC statistical uncertainty for elevated-temperature axial-leakage-corrected keff at BOL, MOL, and EOL. — end of life | Calculated
--- UNCATEGORIZED ---
Uncategorized | BOL Axial Non-Leakage Probability Used For Shielding | 0.97773 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | BOL Core Leakage Source Rate (n/s) | 27869064895158880 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | BOL Radial Leakage Fraction | 0.033088 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | BOL Total Leakage Fraction Used For Shielding | 0.054616 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dynamic Shielding Calculation | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Estimated Shutdown Dose Rate (mrem/h) | 0.11265 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Estimated Shutdown Dose Rate Std Dev (mrem/h) | 0.11265 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Leakage Source Radius Outside Intake Vessel (cm) | 137.9783 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Leakage Source Rate Outside Intake Vessel (n/s) | 13052755234296620 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Activation Step Days | 90 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Batches | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Calculation Directory | /home/hannbn/projects/MARVEL_MRP/Github_repos/mice/MOUSE/shielding_runs/run_20260919T070339Z |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Concrete Activation Zone Boundaries | [5.0, 25.0] |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Concrete Thickness | 200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Confirmation Increment | 5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Decay Days | 90 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Detector Distance | 30 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Detector Radius | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Dose Criterion Met | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Dose Limit | 0.5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Initial Upper Thickness | 60 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Irradiation Years | 60 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Maximum Search Iterations | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Maximum Thickness | 200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Particles | 5000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Batches | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Maximum Retries | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Particles | 50000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Retry Multiplier | 4 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Pit Clearance | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Temperature | 300 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Thickness Tolerance | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Working Directory | /home/hannbn/projects/MARVEL_MRP/Github_repos/mice/MOUSE/shielding_runs |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Vessel Neutron Transmission Fraction | 0.46836 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown