## cost estimate
Account | Account Title | FOAK Estimated Cost ($2025) | NOAK Estimated Cost ($2025) | FOAK Estimated Cost std ($2025) | NOAK Estimated Cost std ($2025) | FOAK LCOE | NOAK LCOE | FOAK LCOE_std | NOAK LCOE_std
10 | Capitalized Pre-Construction Costs | 39646617 | 39646617 | 4002404 | 4002404 | 52 | 52 | 5 | 5
11 | Land Cost | 79950 | 79950 | 14680 | 14680 | 0 | 0 | 0 | 0
12 | Site Permits | 71936 | 71936 | 9052 | 9052 | 0 | 0 | 0 | 0
13 | Plant Licensing | 27823426 | 27823426 | 3448487 | 3448487 | 36 | 36 | 4 | 4
14 | Plant Permits | 5379812 | 5379812 | 1154044 | 1154044 | 7 | 7 | 1 | 1
15 | Plant Studies | 6291491 | 6291491 | 1693597 | 1693597 | 8 | 8 | 2 | 2
20 | Capitalized Direct Costs | 148415169 | 61595600 | 22922065 | 13475139 | 197 | 81 | 30 | 17
21 | Structures and Improvements | 14717183 | 3450105 | 6118291 | 1115300 | 19 | 4 | 8 | 1
211 | Site Preparation/ Yard Work | 205290 | 117972 | 21519 | 12366 | 0 | 0 | 0 | 0
211.1 | Cleaning and Grubbing | 118133 | 67886 | 18553 | 10662 | 0 | 0 | 0 | 0
211.2 | Stripping Topsoil | 71375 | 41016 | 9861 | 5666 | 0 | 0 | 0 | 0
211.3 | Excavation | 15781 | 9068 | 2290 | 1316 | 0 | 0 | 0 | 0
212 | Reactor Island Civil Structures | 1772474 | 1018571 | 366316 | 210507 | 2 | 1 | 0 | 0
212.1 | Reactor Building Slab Roof | 189036 | 108631 | 22913 | 13167 | 0 | 0 | 0 | 0
212.2 | Reactor Building Basement | 152613 | 87700 | 26444 | 15196 | 0 | 0 | 0 | 0
212.3 | Reactor Building Walls | 158143 | 90878 | 23439 | 13469 | 0 | 0 | 0 | 0
212.4 | Reactor Building Liner | 1140422 | 655356 | 364682 | 209568 | 1 | 0 | 0 | 0
212.5 | Reactor Building HVAC | 132258 | 76004 | 53556 | 30776 | 0 | 0 | 0 | 0
213 | Main Function Buildings | 77439 | 44501 | 4581 | 2632 | 0 | 0 | 0 | 0
213.1 | Energy conversion Building | 51901 | 29825 | 3889 | 2235 | 0 | 0 | 0 | 0
213.11 | Energy Conversion Building Slab Roof | 15364 | 8829 | 2404 | 1381 | 0 | 0 | 0 | 0
213.12 | Energy Conversion Building Basement | 12851 | 7385 | 2299 | 1321 | 0 | 0 | 0 | 0
213.13 | Energy Conversion Building Walls | 23685 | 13611 | 3965 | 2279 | 0 | 0 | 0 | 0
213.2 | Control building | 25538 | 14675 | 2452 | 1409 | 0 | 0 | 0 | 0
213.21 | Control Building Slab Roof | 7673 | 4409 | 1406 | 808 | 0 | 0 | 0 | 0
213.22 | Control Building Basement | 6350 | 3649 | 1275 | 733 | 0 | 0 | 0 | 0
213.23 | Control Building Walls | 11513 | 6616 | 1968 | 1131 | 0 | 0 | 0 | 0
214 | Buildings to Support Main Function | 12620231 | 2245069 | 6068514 | 1072485 | 16 | 2 | 8 | 1
214.7 | Emergency and Start-up Power Systems Building | 12582557 | 2223419 | 6068167 | 1072284 | 16 | 2 | 8 | 1
214.72 | Diesel Generator | 12582557 | 2223419 | 6068167 | 1072284 | 16 | 2 | 8 | 1
214.8 | Auxilliary Building | 37674 | 21650 | 4035 | 2319 | 0 | 0 | 0 | 0
214.81 | Maniplator Building | 37674 | 21650 | 4035 | 2319 | 0 | 0 | 0 | 0
214.811 | Manipulator Building Slab Roof | 6360 | 3655 | 824 | 473 | 0 | 0 | 0 | 0
214.812 | ManipulatorBuilding Basement | 18125 | 10416 | 3174 | 1824 | 0 | 0 | 0 | 0
214.813 | Manipulator Building Exterior Walls | 13188 | 7578 | 1987 | 1142 | 0 | 0 | 0 | 0
215 | Supply Chain Buildings | 41747 | 23990 | 4304 | 2473 | 0 | 0 | 0 | 0
215.1 | Storage Building | 41747 | 23990 | 4304 | 2473 | 0 | 0 | 0 | 0
215.11 | Storage Building Slab Roof | 17182 | 9874 | 3158 | 1815 | 0 | 0 | 0 | 0
215.12 | Storage Building Basement | 12152 | 6983 | 2254 | 1295 | 0 | 0 | 0 | 0
215.13 | Storage Building Walls | 12411 | 7132 | 1767 | 1015 | 0 | 0 | 0 | 0
22 | Reactor System | 91431231 | 26646057 | 15007717 | 3235816 | 121 | 35 | 19 | 4
221 | Reactor Components | 71812992 | 14080325 | 14473448 | 2597559 | 95 | 18 | 19 | 3
221.1 | Reactor Vessel and Accessories | 17785413 | 4590068 | 2022905 | 522072 | 23 | 6 | 2 | 0
221.11 | Reactor Support | 2906619 | 750141 | 480450 | 123994 | 3 | 0 | 0 | 0
221.12 | Outer Vessel Structure - stainless_steel | 2095355 | 540770 | 346486 | 89421 | 2 | 0 | 0 | 0
221.13 | Inner Vessel Structure - stainless_steel | 12783439 | 3299156 | 1873431 | 483496 | 16 | 4 | 2 | 0
221.2 | Reactor Control Devices | 5275283 | 875408 | 298522 | 49350 | 7 | 1 | 0 | 0
221.21 | Reactivity Control System | 5275283 | 875408 | 298522 | 49350 | 7 | 1 | 0 | 0
221.211 | Reactivity Control System Fabrication | 2281999 | 364094 | 241902 | 38595 | 3 | 0 | 0 | 0
221.212 | Installation | 533720 | 85155 | 67596 | 10785 | 0 | 0 | 0 | 0
221.213 | Control Drums Materials (Absorber) - B4C_enriched | 1602591 | 283188 | 171150 | 30243 | 2 | 0 | 0 | 0
221.214 | Control Drums Materials (Reflector) - Graphite | 253887 | 44863 | 42144 | 7447 | 0 | 0 | 0 | 0
221.215 | Control System Drive Mechanism | 493245 | 78697 | 82841 | 13217 | 0 | 0 | 0 | 0
221.216 | Shutdown Rod Absorber Material - B4C_enriched | 98879 | 17472 | 0 | 0 | 0 | 0 | 0 | 0
221.217 | Shutdown Rod Cladding Material - SS304 | 10959 | 1936 | 0 | 0 | 0 | 0 | 0 | 0
221.3 | Non-Fuel Core Internals | 48752295 | 8614847 | 14243283 | 2516880 | 64 | 11 | 18 | 3
221.31 | Reflector | 267859 | 47332 | 30322 | 5358 | 0 | 0 | 0 | 0
221.311 | Radial Reflector - Graphite | 114455 | 20224 | 21167 | 3740 | 0 | 0 | 0 | 0
221.312 | Axial Reflector - Graphite | 153404 | 27107 | 24678 | 4360 | 0 | 0 | 0 | 0
221.32 | Shield | 46932256 | 8293235 | 14191016 | 2507644 | 62 | 11 | 18 | 3
221.321 | In Vessel Shield Materials - B4C_natural | 46435361 | 8205430 | 14202874 | 2509740 | 61 | 10 | 18 | 3
221.322 | Out The Vessel Shield Materials - WEP | 496895 | 87804 | 110881 | 19593 | 0 | 0 | 0 | 0
221.33 | Moderator - ZrH | 1552178 | 274280 | 269513 | 47624 | 2 | 0 | 0 | 0
222 | Main Heat Transport System | 6731468 | 5054481 | 950127 | 715715 | 8 | 6 | 1 | 0
222.1 | Fluid Circulation Drive System | 1168832 | 206540 | 607030 | 107266 | 1 | 0 | 0 | 0
222.11 | Primary Pump - Yes | 1168832 | 206540 | 607030 | 107266 | 1 | 0 | 0 | 0
222.2 | Reactor Heat Transfer Piping System - LTMR | 186398 | 32937 | 27261 | 4817 | 0 | 0 | 0 | 0
222.3 | Heat Exchangers | 681693 | 120459 | 93518 | 16525 | 0 | 0 | 0 | 0
222.31 | Primary Heat Exchanger - SS316 | 681693 | 120459 | 93518 | 16525 | 0 | 0 | 0 | 0
222.5 | Initial Coolant Inventory - NaK | 4694544 | 4694544 | 700135 | 700135 | 6 | 6 | 0 | 0
223 | Safety Systems | 2503815 | 442440 | 255849 | 45210 | 3 | 0 | 0 | 0
223.2 | Reactor Cavity Cooling System (Rvacs) | 2503815 | 442440 | 255849 | 45210 | 3 | 0 | 0 | 0
223.21 | Rvacs (Cooling Vessel) | 1189558 | 210202 | 223761 | 39540 | 1 | 0 | 0 | 0
223.22 | Rvacs (Intake Vessel) | 1314257 | 232237 | 161519 | 28541 | 1 | 0 | 0 | 0
226 | Other Reactor Plant Equipment - LTMR | 552732 | 97671 | 126798 | 22406 | 0 | 0 | 0 | 0
227 | Reactor Instrumentation and Control (I&C) | 9792373 | 6964449 | 2338717 | 1663323 | 13 | 9 | 3 | 2
228 | Reactor Plant Miscellaneous Items | 37848 | 6688 | 8579 | 1516 | 0 | 0 | 0 | 0
23 | Energy Conversion System | 19415741 | 13808700 | 19754154 | 14049384 | 25 | 18 | 26 | 18
232 | Energy Applications | 18201415 | 12945057 | 19763912 | 14056323 | 24 | 17 | 26 | 18
232.1 | Electricity Generation Systems | 18201415 | 12945057 | 19763912 | 14056323 | 24 | 17 | 26 | 18
236 | Common Instrumentation & Controls | 1214325 | 863642 | 199330 | 141766 | 1 | 1 | 0 | 0
24 | Electrical Equipment | 11249883 | 8001047 | 2984691 | 2122747 | 14 | 10 | 3 | 2
241 | Switchgear | 1051538 | 747866 | 657543 | 467652 | 1 | 0 | 0 | 0
242 | Station Service Equipment | 801047 | 569714 | 393899 | 280146 | 1 | 0 | 0 | 0
243 | Switchboards | 261692 | 186118 | 104082 | 74024 | 0 | 0 | 0 | 0
244 | Protective Equipment | 773979 | 550463 | 522978 | 371948 | 1 | 0 | 0 | 0
245 | Electrical Structure & Wiring Container | 4114716 | 2926433 | 2264496 | 1610536 | 5 | 3 | 3 | 2
246 | Power & Control Wiring | 4246908 | 3020450 | 2535711 | 1803427 | 5 | 4 | 3 | 2
25 | Initial Fuel Inventory | 10100741 | 9424560 | 1709224 | 1704561 | 13 | 12 | 2 | 2
251 | First Core Mining | 6027893 | 6027893 | 846097 | 846097 | 8 | 8 | 1 | 1
252 | First Core Conversion | 474978 | 474978 | 50359 | 50359 | 0 | 0 | 0 | 0
253 | First Core Enrichment | 2776557 | 2776557 | 1332371 | 1332371 | 3 | 3 | 1 | 1
254 | First Core Fuel Assembly Fabrication - No - UO2 | 821311 | 145131 | 120098 | 21222 | 1 | 0 | 0 | 0
26 | Miscellaneous Equipment (Cranes) | 1500387 | 265128 | 359810 | 63580 | 1 | 0 | 0 | 0
30 | Capitalized Indirect Services Cost | 14692912 | 6180543 | 2392605 | 1248005 | 19 | 8 | 3 | 1
31 | Factory & field indirect costs | 8210631 | 2870936 | 1541993 | 924718 | 10 | 3 | 2 | 1
32 | Factory and construction supervision | 1416969 | 398771 | 895114 | 268245 | 1 | 0 | 1 | 0
33 | Startup Costs | 2837837 | 1630794 | 603833 | 346999 | 3 | 2 | 0 | 0
34 | Shipping and Transportation Costs | 1047842 | 602154 | 277279 | 159341 | 1 | 0 | 0 | 0
35 | Engineering Services | 668022 | 383886 | 106455 | 61175 | 0 | 0 | 0 | 0
36 | PM/CM Services | 511608 | 294001 | 128494 | 73840 | 0 | 0 | 0 | 0
40 | Capitalized training costs | 344522 | 344522 | 67917 | 67917 | 0 | 0 | 0 | 0
41 | staff recruitment and training | 344522 | 344522 | 67917 | 67917 | 0 | 0 | 0 | 0
60 | Capitalized Financial Costs | 3505460 | 1860046 | 435069 | 251801 | 4 | 2 | 0 | 0
62 | Interest | 3505460 | 1860046 | 435069 | 251801 | 4 | 2 | 0 | 0
70 | Annualized O&M Cost | 6753890 | 3099203 | 683723 | 431057 | 125 | 57 | 12 | 8
71 | O&M Staff | 1124474 | 1124474 | 140322 | 140322 | 20 | 20 | 2 | 2
711 | Operators | 6372 | 6372 | 1034 | 1034 | 0 | 0 | 0 | 0
712 | Remote Monitoring Technicians - Remotely Monitored | 114128 | 114128 | 19518 | 19518 | 2 | 2 | 0 | 0
713 | Security Staff | 1003973 | 1003973 | 137882 | 137882 | 18 | 18 | 2 | 2
73 | Regulatory Costs | 120704 | 120704 | 26044 | 26044 | 2 | 2 | 0 | 0
75 | Capital Plant Expenditures | 5420497 | 1806534 | 675857 | 411365 | 101 | 33 | 12 | 7
751 | Annualized Outer Vessel Structure Replacements | 197786 | 51044 | 32705 | 8440 | 3 | 0 | 0 | 0
752 | Annualized Inner Vessel Structure Replacements | 1998136 | 515680 | 292829 | 75573 | 37 | 9 | 5 | 1
753 | Annualized Moderator Replacements | 422897 | 74728 | 73430 | 12975 | 7 | 1 | 1 | 0
754 | Annualized Reflector Replacements | 41868 | 7398 | 4739 | 837 | 0 | 0 | 0 | 0
755 | Annualized Reactor Control Devices Replacements | 824561 | 136832 | 46661 | 7713 | 15 | 2 | 0 | 0
759 | Annualized Plant Maintenance (Misc.) | 1935246 | 1020850 | 688518 | 427317 | 36 | 19 | 12 | 7
759.1 | Annualized Building and Structural Maintenance (Accounts 212–215) | 435356 | 99964 | 183242 | 33274 | 8 | 1 | 3 | 0
759.2 | Annualized Main Heat Transport System Maintenance (Accounts 222.1–222.3 and 222.6) | 61107 | 10798 | 17734 | 3133 | 1 | 0 | 0 | 0
759.3 | Annualized Safety System Maintenance (Account 223) | 75114 | 13273 | 7675 | 1356 | 1 | 0 | 0 | 0
759.4 | Annualized Reactor Plant Equipment Maintenance (Accounts 221.11, 226, and 228) | 104915 | 25635 | 14964 | 3789 | 1 | 0 | 0 | 0
759.5 | Annualized Reactor I&C Maintenance (Account 227) | 293771 | 208933 | 70161 | 49899 | 5 | 3 | 1 | 0
759.6 | Annualized Energy Conversion System Maintenance (Account 23) | 582472 | 414261 | 592624 | 421481 | 10 | 7 | 11 | 7
759.7 | Annualized Electrical Equipment Maintenance (Account 24) | 337496 | 240031 | 89540 | 63682 | 6 | 4 | 1 | 1
759.8 | Annualized Miscellaneous Equipment Maintenance (Account 26) | 45011 | 7953 | 10794 | 1907 | 0 | 0 | 0 | 0
78 | Annualized Decommissioning Cost | 88213 | 47489 | 10845 | 6327 | 1 | 0 | 0 | 0
80 | Annualized Fuel Cost | 2815836 | 2631607 | 464793 | 463656 | 52 | 49 | 8 | 8
81 | Refueling Operations | 3299 | 3299 | 502 | 502 | 0 | 0 | 0 | 0
82 | Additional Nuclear Fuel | 2751991 | 2567763 | 465685 | 464415 | 51 | 47 | 8 | 8
83 | Spent Fuel Management | 60545 | 60545 | 9815 | 9815 | 1 | 1 | 0 | 0
OCC | Overnight Capital Cost | 203099221 | 107767283 | 25207024 | 14588851 | - | - | - | -
OCC per kW | Overnight Capital Cost per kW | 32757 | 17381 | 4065 | 2353 | - | - | - | -
OCC excl. fuel | Overnight Capital Cost Excluding Fuel | 192998480 | 98342722 | 25547833 | 14778070 | - | - | - | -
OCC excl. fuel per kW | Overnight Capital Cost Excluding Fuel per kW | 31128 | 15861 | 4120 | 2383 | - | - | - | -
TCI | Total Capital Investment | 206604682 | 109627330 | 25642094 | 14840652 | - | - | - | -
TCI per kW | Total Capital Investment per kW | 33323 | 17681 | 4135 | 2393 | - | - | - | -
OCC (ITC-adjusted) | Overnight Capital Cost Adjusted for the Investment Tax Credit | 148262431 | 107767283 | 18401128 | 14588851 | - | - | - | -
OCC (ITC-adjusted) per kW | Overnight Capital Cost Adjusted for the Investment Tax Credit per kW | 23913 | 17381 | 2967 | 2353 | - | - | - | -
TCI (ITC-adjusted) | Total Capital Investment Adjusted for the Investment Tax Credit | 151767892 | 109627330 | 18836197 | 14840652 | - | - | - | -
TCI (ITC-adjusted) per kW | Total Capital Investment Adjusted for the Investment Tax Credit per kW | 24478 | 17681 | 3038 | 2393 | - | - | - | -
AC | Annualized Cost | 9569726 | 5730810 | 756440 | 552682 | - | - | - | -
AC per MWh | Annualized Cost per MWh | 178 | 106 | 14 | 10 | - | - | - | -
LCOE | Levelized Cost Of Energy ($/MWh) | 453 | 252 | 44 | 27 | - | - | - | -
LCOE (ITC-adjusted) | Levelized Cost Of Energy Adjusted for the Investment Tax Credit ($/MWh) | 380 | 252 | 35 | 27 | - | - | - | -
LCOH | Levelized Cost Of Heat ($/MWth) | 121 | 67 | 11 | 7 | - | - | - | -

## Parameters
Group | Parameter | Value | Units | Description | Source
--- SETTINGS ---
Settings | Parametric Screening Mode | TRUE |  | Reduced-cost comparison mode: temperature coefficient at BOL and nearest saved EOL, shutdown margin at BOL, and non-blocking central-value constraint flags. | User Input
Settings | cross_sections_xml_location | /projects/MRP_MOUSE/openmc_data/endfb-viii.0-hdf5/cross_sections.xml |  | File path to the OpenMC cross sections XML file on HPC | User Input
Settings | plotting | N |  | Whether to generate and save geometry plots (Y = yes, N = no) | User Input
Settings | simplified_chain_thermal_xml | /projects/MRP_MOUSE/openmc_data/chain_endf_b8.0.xml |  | File path to the simplified depletion chain XML file for thermal reactors | User Input
--- MATERIALS ---
Materials | Axial Reflector | Graphite |  | Axial reflector material type — may differ from radial reflector | User Input
Materials | Common Temperature | 600 | K | Uniform operating temperature applied to all materials in isothermal simulations | User Input
Materials | Control Drum Absorber | B4C_enriched |  | Neutron absorber material in the control drums (e.g. B4C_enriched, B4C_natural) | User Input
Materials | Control Drum Reflector | Graphite |  | Reflector material in the control drums (e.g. Graphite) | User Input
Materials | Coolant | NaK |  | Primary coolant material type (e.g. NaK, Helium) | User Input
Materials | Enrichment | 0.05 | fraction | Uranium-235 enrichment fraction (0 to 1) | User Input
Materials | Fuel | UO2 |  | Primary fuel material type (e.g. TRIGA_fuel, UO2, UN, UC, homog_TRISO) | User Input
Materials | HX Material | SS316 |  | Heat exchanger structural material (e.g. SS316) | User Input
Materials | Moderator | ZrH |  | Neutron moderator material type (e.g. ZrH, Graphite, monolith_graphite) | User Input
Materials | Radial Reflector | Graphite |  | Radial reflector material type (e.g. Graphite, BeO) | User Input
Materials | Shutdown Rod Absorber | B4C_enriched |  | Neutron absorber material used in the movable shutdown rods | User Input
Materials | Shutdown Rod Cladding | SS304 |  | Cladding material that moves with each shutdown-rod absorber | User Input
Materials | TRISO Fueled | No |  | Whether the reactor uses TRISO fuel particles (Yes or No) | User Input
Materials | reactor type | LTMR |  | Reactor type identifier: LTMR (liquid metal thermal), GCMR (gas-cooled), or HPMR (heat pipe) | User Input
--- GEOMETRY ---
Geometry | Active Height | 120 | cm | Axial height of the active fuel region | User Input
Geometry | Assembly FTF | 77.1455 | cm | Assembly flat-to-flat distance (distance between opposite parallel faces of the hexagonal assembly). | User Input or Calculated
Geometry | Axial Reflector Thickness | 44.54 | cm | Thickness of each axial neutron reflector (top and bottom) | User Input
Geometry | Core Radius | 83.1128 | cm | Total core radius including the radial reflector | User Input or Calculated
Geometry | Fuel Pin Count | 408 |  | Total number of fuel pins (or fuel elements) in the entire core | Calculated
Geometry | Fuel Pin Materials | ['Zr', None, 'UO2', None, 'SS304'] |  | Ordered list of materials for each fuel pin region from innermost to outermost | User Input
Geometry | Fuel Pin Radii | [0.28575, 0.3175, 1.5113, 1.5367, 1.5875] | cm | Ordered list of radii defining fuel pin region boundaries from innermost to outermost | User Input
Geometry | Lattice Apothem | 38.5728 | cm | Distance from the hex lattice center to the midpoint of a flat face of the outermost pin lattice. | Calculated
Geometry | Lattice Radius | 38.5728 | cm | Legacy LTMR name for the hex lattice apothem: distance from the hex lattice center to the midpoint of a flat face. | Calculated
Geometry | Moderator Pin Count | 133 |  | Total number of moderator pins in the entire core | Calculated
Geometry | Moderator Pin Inner Radius | 1.5367 | cm | Inner radius of the moderator pin cladding | User Input
Geometry | Moderator Pin Materials | ['ZrH', 'SS304'] |  | Ordered list of materials for each moderator pin region from innermost to outermost | User Input
Geometry | Moderator Pin Radii | [1.5367, 1.5875] | cm | Ordered list of radii defining moderator pin region boundaries | User Input
Geometry | Number of Rings per Assembly | 14 |  | Number of pin rings along the side of the hexagonal assembly (LTMR/HPMR) | User Input
Geometry | Number of Shutdown Rods | 6 |  | Total shutdown-rod count. LTMR accepts user-selected 6- or 12-rod predefined layouts; GCMR calculates the total from the central and surrounding assembly inputs. | User Input or Calculated
Geometry | Pin Gap Distance | 0.1 | cm | Gap distance between adjacent pins (center-to-center minus two outer radii) | User Input
Geometry | Radial Reflector Thickness | 44.54 | cm | Thickness of the radial neutron reflector surrounding the active core | User Input
Geometry | Shutdown Rod Absorber Radius | 1.3 | cm | Outer radius of the LTMR shutdown-rod B4C absorber | User Input
Geometry | Shutdown Rod Clad Radius | 1.5 | cm | Outer radius of the LTMR shutdown-rod cladding | User Input
Geometry | Shutdown Rod Height | 120 | cm | Physical height of each LTMR shutdown rod; defaults to the active core height in the example input | User Input
--- CONTROL DRUMS ---
Control Drums | All Drum Tubes Area | 9348.4914 | cm² | Total cross-sectional area removed from the reflector by all control-drum tubes, including clearance around each physical drum | Calculated
Control Drums | All Drums Area | 9144.1589 | cm² | Total cross-sectional area of all control drums | Calculated
Control Drums | All Drums Volume | 1911860.7239 | cm³ | Total volume of all control drums combined | Calculated
Control Drums | Control Drum Absorber Mass | 142.5186 | kg | Total mass of absorber material in all control drums | Calculated
Control Drums | Control Drum Reflector Mass | 2968.4892 | kg | Total mass of reflector material in all control drums | Calculated
Control Drums | Control Drums Mass | 3111.0078 | kg | Total combined mass of all control drums (absorber + reflector) | Calculated
Control Drums | Drum Absorber Arc Degrees | 120 | degrees | Angular span of the absorber arc on each control drum; used by both OpenMC geometry and material inventory calculations | User Input
Control Drums | Drum Absorber Thickness | 1 | cm | Thickness of the absorber arc section within each control drum | User Input
Control Drums | Drum Count | 6 |  | Total number of control drums in the core; explicit and validated against the GCMR lattice. | User Input or Calculated
Control Drums | Drum Height | 209.08 | cm | Height of the control drums (typically active height + 2x axial reflector thickness) | User Input
Control Drums | Drum Radius | 22.0253 | cm | Outer radius of each control drum. If not specified, it is automatically set to the largest allowable value that avoids drum overlap. | User Input
Control Drums | Drum Tube Radius | 22.27 | cm | Outer radius of the control drum tube. It is explicit and validated for the GCMR example and may be calculated for other models. | User Input or Calculated
Control Drums | Number of Drums | 6 |  | Number of control drums in the core (e.g. 6, 12) | User Input
--- CORE DESIGN ---
Core Design | Axial Reflector Mass | 1760.6185 | kg | Total mass of both axial reflectors (top and bottom combined) | Calculated
Core Design | Axial Reflector Volume | 1100386.5456 | cm³ | Combined volume of both LTMR axial reflectors, excluding control-drum tubes | Calculated
Core Design | Moderator Mass | 663.0541 | kg | Total mass of the neutron moderator material in the core | Calculated
Core Design | Radial Reflector Mass | 1382.1498 | kg | Total mass of the radial neutron reflector | Calculated
Core Design | Radial Reflector Volume | 863843.6138 | cm³ | LTMR radial reflector volume over the active core height, excluding the hexagonal core and control-drum tubes | Calculated
Core Design | Shutdown Rod Absorber Mass | 9.6332 | kg | Total B4C absorber mass in all shutdown rods | Calculated
Core Design | Shutdown Rod Absorber Volume | 3822.6899 | cm³ | Total B4C absorber volume in all shutdown rods | Calculated
Core Design | Shutdown Rod Cladding Mass | 10.1082 | kg | Total cladding mass in all shutdown rods | Calculated
Core Design | Shutdown Rod Cladding Volume | 1266.6902 | cm³ | Total cladding volume in all shutdown rods | Calculated
Core Design | Shutdown Rods Mass | 19.7414 | kg | Combined absorber and cladding mass of all shutdown rods | Calculated
--- OVERALL SYSTEM ---
Overall System | Burnup Steps | [0.1, 0.5, 1.0, 2.0, 5.0, 10.0, 15.0, 20.0, 40.0, 80.0, 120.0, 140.0] | MWd/kg | Cumulative burnup values at each depletion time step | User Input
Overall System | Heat Flux | 0.40954 | MW/m² | Calculated average fuel surface heat flux at full power | Calculated
Overall System | Heat Flux Criteria | 0.9 | MW/m² | Maximum allowable fuel surface heat flux (design constraint) | User Input
Overall System | Power MWe | 6.2 | MWe | Reactor net electric power output (thermal power × thermal efficiency) | Calculated
Overall System | Power MWt | 20 | MWt | Reactor thermal power output | User Input
Overall System | Thermal Efficiency | 0.31 | fraction | Net thermal-to-electric conversion efficiency of the power conversion system | User Input
--- OPENMC SETTINGS ---
OpenMC Settings | Cold Shutdown Temperature | 300 | K | Temperature used for the shutdown-state (ARI) keff calculation during shutdown margin evaluation. | User Input
OpenMC Settings | Depletion Integrator | predictor |  | Requested depletion integration method: predictor or cecm. | User Input
OpenMC Settings | Depletion Integrator Used | predictor |  | Depletion integration method actually used by the calculation. | Calculated
OpenMC Settings | Isothermal Temperature Coefficients | TRUE |  | Whether isothermal temperature reactivity coefficients were calculated | User Input
OpenMC Settings | Maximum Temperature Coefficient | -1 | pcm/K | Maximum allowed central-value temperature coefficient at both BOL and EOL for the parametric-screening pass/fail flag. | User Input
OpenMC Settings | Minimum Shutdown Margin | 1000 | pcm | Central-value BOL shutdown-margin threshold used for reporting the parametric-screening pass/fail flag. | User Input
OpenMC Settings | Shutdown Margin Calc | TRUE |  | Whether shutdown margin is calculated. When True, the shutdown-state keff is evaluated with the absorber facing the core (ARI) at Cold Shutdown Temperature, and shutdown margin metrics are reported from ((1 - k_s) / k_s). | User Input
OpenMC Settings | Temperature Coefficient Particles Per Batch | 4000 | particles/batch | OpenMC particle histories per batch for each parametric-screening temperature-coefficient static calculation. | User Input
OpenMC Settings | Temperature Perturbation | 100 | K | Temperature increase applied for isothermal temperature coefficient calculation | User Input
--- PHYSICS RESULTS ---
Physics Results | BOL Axial Non-Leakage Probability | 0.98304 | fraction | Beginning-of-life axial non-leakage probability from the 2D-to-3D buckling correction model. | Calculated
Physics Results | BOL Total Non-Leakage Probability | 0.92623 | fraction | Beginning-of-life total non-leakage probability from the axial-plus-radial buckling model. Returns NaN when Core Radius is not available. | Calculated
Physics Results | Depletion Time Steps | [0.0, 15.407, 77.0348, 154.0696, 308.1392, 770.348, 1540.6959, 2311.0439, 3081.3919, 6162.7837, 12325.5674, 18488.3511, 21569.743] | days | Calculated cumulative depletion times corresponding to the reported keff values and used as the x-axis in keff_comparison_vs_Time.png. | Calculated
Physics Results | Estimated Axial Leakage (%) | 1.6959 | % | Estimated beginning-of-life axial neutron leakage percentage from the axial buckling correction model, computed as 100 × (1 - axial non-leakage probability). | Calculated
Physics Results | Estimated Total Leakage (%) | 7.3765 | % | Estimated beginning-of-life total neutron leakage percentage from the axial-plus-radial buckling model, computed as 100 × (1 - total non-leakage probability). Returns NaN when Core Radius is not available. | Calculated
Physics Results | Fuel Lifetime | 1593 | days | Estimated fuel cycle length — time for the 3D-corrected keff to fall to 1.0 | Calculated
Physics Results | Fuel Lifetime Extrapolated | FALSE |  | True when fuel lifetime was extrapolated beyond the simulated depletion schedule from the final two corrected keff points. | Calculated
Physics Results | Fuel Lifetime Status | Interpolated k=1 crossing |  | Whether fuel lifetime came from an interpolated k=1 crossing, BOL-subcritical result, terminal extrapolation, or simulated endpoint lower bound. | Calculated
Physics Results | Fuel Tail Waste Mass | 28717.9307 | kg | Mass of depleted uranium tails produced during the enrichment process | Calculated
Physics Results | Lifecycle Evaluation Times (BOL) | 0 | days | Actual saved-state times used for lifecycle safety evaluations. Screening mode reports BOL and nearest-saved EOL; detailed mode reports BOL, MOL, and interpolated EOL. — beginning of life | Calculated
Physics Results | Lifecycle Evaluation Times (EOL) | 1540.6959 | days | Actual saved-state times used for lifecycle safety evaluations. Screening mode reports BOL and nearest-saved EOL; detailed mode reports BOL, MOL, and interpolated EOL. — end of life | Calculated
Physics Results | Mass U235 | 154069.5929 | g | Initial mass of U-235 in the fresh fuel load | Calculated
Physics Results | Mass U238 | 2925242.3256 | g | Initial mass of U-238 in the fresh fuel load | Calculated
Physics Results | Max Peaking Factor | 1.8858 | unitless | Maximum pin peaking factor among saved depletion states at or before the calculated end of operating life | Calculated
Physics Results | Max Peaking Factors per Step | [1.840761698592251, 1.8458637751970373, 1.8803129838873802, 1.8857711738400864, 1.798814015999095, 1.860003784462648, 1.770335032081474] | unitless | List of the maximum pin peaking factor at each saved depletion state at or before EOL, in step order | Calculated
Physics Results | Maximum Shutdown Margin 3D (2D corrected) | 4407.7244 | pcm | Maximum shutdown margin among the BOL, MOL, and EOL evaluations after correcting shutdown-state keff from 2D to 3D using the axial leakage approximation. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) | 4407.7244 | pcm | Minimum shutdown margin among the BOL, MOL, and EOL evaluations after correcting shutdown-state keff from 2D to 3D using the axial leakage approximation. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) Point | BOL |  | Lifecycle point, BOL, MOL, or EOL, at which the minimum axial-leakage-corrected shutdown margin occurs. | Calculated
Physics Results | Most Limiting Shutdown Margin 3D (2D corrected) Uncertainty | 352.6824 | pcm | One standard deviation OpenMC statistical uncertainty associated with the reported minimum axial-leakage-corrected shutdown margin. Axial leakage model uncertainty is excluded. | Calculated
Physics Results | Natural Uranium Mass | 31797.2426 | kg | Mass of natural uranium feed required to produce the enriched fuel | Calculated
Physics Results | Parametric Screening Pass | FALSE |  | Combined shutdown-margin and temperature-coefficient screening result. Reporting only; all engineering and cost calculations still run. | Calculated
Physics Results | Region ID with Max Peaking Factor | 222 | unitless | Region ID with the highest peaking factor among saved depletion states at or before EOL; for LTMR this is typically a pin/distribcell ID, while for GCMR it is a mesh-region index | Calculated
Physics Results | SWU | 24466.4569 | kg-SWU | Separative work units required to produce the enriched fuel | Calculated
Physics Results | Shutdown Margin 3D (2D corrected) Lifecycle (BOL) | 4407.7244 | pcm | Subcritical margin relative to criticality at the configured lifecycle points using cold shutdown keff corrected from 2D to 3D. Screening mode reports BOL only. — beginning of life | Calculated
Physics Results | Shutdown Margin 3D (2D corrected) Lifecycle Uncertainty (BOL) | 352.6824 | pcm | One standard deviation OpenMC statistical uncertainty for the reported axial-leakage-corrected shutdown margin evaluations. Axial leakage model uncertainty is excluded. — beginning of life | Calculated
Physics Results | Shutdown Margin Constraint Pass | TRUE |  | Central-value BOL shutdown margin satisfies the screening threshold. Reporting only; it does not stop the run. | Calculated
Physics Results | Step with Max Peaking Factor | 4 | unitless | Saved depletion step at or before EOL at which the maximum peaking factor occurs | Calculated
Physics Results | Temp Coeff 3D (2D corrected) | 1.1693 | pcm/K | Most limiting, numerically largest isothermal temperature coefficient among the BOL, MOL, and EOL evaluations, corrected from 2D to 3D using axial neutron leakage correction. Negative values confirm self-stabilizing behavior. Use this value for safety analysis. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle (BOL) | 1.1693 | pcm/K | Isothermal temperature coefficient evaluated at the configured lifecycle points and corrected from 2D to 3D using the axial leakage approximation. — beginning of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle (EOL) | 0.17352 | pcm/K | Isothermal temperature coefficient evaluated at the configured lifecycle points and corrected from 2D to 3D using the axial leakage approximation. — end of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle Uncertainty (BOL) | 2.8906 | pcm/K | One standard deviation OpenMC statistical uncertainty for the reported axial-leakage-corrected lifecycle temperature coefficient evaluations. Axial leakage model uncertainty is excluded. — beginning of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Lifecycle Uncertainty (EOL) | 3.0331 | pcm/K | One standard deviation OpenMC statistical uncertainty for the reported axial-leakage-corrected lifecycle temperature coefficient evaluations. Axial leakage model uncertainty is excluded. — end of life | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Limiting Point | BOL |  | Lifecycle point, BOL, MOL, or EOL, at which the limiting axial-leakage-corrected isothermal temperature coefficient occurs. | Calculated
Physics Results | Temp Coeff 3D (2D corrected) Uncertainty | 2.8906 | pcm/K | One standard deviation OpenMC statistical uncertainty associated with the reported limiting axial-leakage-corrected temperature coefficient. Axial leakage model uncertainty is excluded. | Calculated
Physics Results | Temperature Coefficient Constraint Pass | FALSE |  | Central-value BOL and EOL temperature coefficients satisfy the screening threshold. Reporting only; it does not stop the run. | Calculated
Physics Results | Uranium Mass | 3079.3119 | kg | Total initial uranium mass in the fresh fuel load (U-235 + U-238) | Calculated
Physics Results | keff 3D (2D corrected) | [1.0956045144617417, 1.0788995454077681, 1.0755937729331295, 1.0708090863723039, 1.0561637613026613, 1.0331802037602327, 1.0019821597869143, 0.9728795298387218, 0.942824184603042, 0.8629595278839396, 0.7463456164537183, 0.6897331316954834, 0.6745670100240521] |  | keff at each burnup step for the operating configuration (ARO), corrected from 2D to 3D using axial leakage correction and evaluated at Common Temperature. | Calculated
--- PRIMARY LOOP & BALANCE OF PLANT ---
Primary Loop & Balance of Plant | BoP Count | 2 |  | Number of Balance of Plant (power conversion) systems | User Input
Primary Loop & Balance of Plant | BoP Power kWe | 3100 | kWe | Electric power handled by each BoP system | Calculated
Primary Loop & Balance of Plant | BoP per loop load fraction | 0.5 | fraction | Fraction of total electric load handled by each BoP system | User Input
Primary Loop & Balance of Plant | Coolant Mass Flow Rate | 226.2955 | kg/s | Total primary coolant mass flow rate | Calculated
Primary Loop & Balance of Plant | Primary HX Mass | 5208.2253 | kg | Calculated mass of the primary heat exchanger | Calculated
Primary Loop & Balance of Plant | Primary Loop Inlet Temperature | 703.15 | K | Primary coolant temperature at the core inlet | User Input
Primary Loop & Balance of Plant | Primary Loop Mass Flow Rate | 226.2955 | kg/s | Coolant mass flow rate per primary loop | Calculated
Primary Loop & Balance of Plant | Primary Loop Outlet Temperature | 793.15 | K | Primary coolant temperature at the core outlet | User Input
Primary Loop & Balance of Plant | Primary Pump | Yes |  | Whether a primary coolant pump is present (Yes or No) | User Input
Primary Loop & Balance of Plant | Primary Pump Mechanical Power | 94.2898 | kW | Mechanical power required to drive the primary coolant pump | Calculated
Primary Loop & Balance of Plant | Pump Isentropic Efficiency | 0.8 | fraction | Isentropic efficiency of the primary coolant pump | User Input
Primary Loop & Balance of Plant | Secondary HX Mass | 0 | kg | Mass of the secondary heat exchanger (0 if none) | User Input
Primary Loop & Balance of Plant | Secondary Loop Inlet Temperature | 668.15 | K | Secondary loop coolant temperature at the heat exchanger inlet | User Input
Primary Loop & Balance of Plant | Secondary Loop Outlet Temperature | 768.15 | K | Secondary loop coolant temperature at the heat exchanger outlet | User Input
Primary Loop & Balance of Plant | Secondary Pump | No |  | Whether a secondary coolant pump is present (Yes or No) | User Input
--- SHIELDING ---
Shielding | In Vessel Shield Inner Radius | 83.1128 | cm | Inner radius of the in-vessel radiation shield (equal to core radius) | User Input
Shielding | In Vessel Shield Mass | 4342.4762 | kg | Total mass of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Material | B4C_natural |  | Material of the in-vessel radiation shield | User Input
Shielding | In Vessel Shield Outer Radius | 93.2728 | cm | Outer radius of the in-vessel radiation shield | Calculated
Shielding | In Vessel Shield Thickness | 10.16 | cm | Thickness of the in-vessel radiation shield (0 if none) | User Input
Shielding | Out Of Vessel Shield Effective Density Factor | 0.5 | fraction | Effective density factor for the out-of-vessel shield — accounts for partial fill (e.g. 0.5 = 50% fill) | User Input
Shielding | Out Of Vessel Shield Mass | 27797.6147 | kg | Total mass of the out-of-vessel radiation shield | Calculated
Shielding | Out Of Vessel Shield Material | WEP |  | Material of the out-of-vessel radiation shield | User Input
Shielding | Out Of Vessel Shield Thickness | 100 | cm | Thickness of the out-of-vessel radiation shield | User Input
Shielding | Outer Shield Inner Radius | 112.2728 | cm | Inner radius of the out-of-vessel shield | Calculated
Shielding | Outer Shield Outer Radius | 212.2728 | cm | Outer radius of the out-of-vessel shield (outermost boundary of the shielded assembly) | Calculated
--- VESSELS ---
Vessels | Cooling Vessel Mass | 1004.5136 | kg | Total mass of the cooling vessel | Calculated
Vessels | Cooling Vessel Material | stainless_steel |  | Structural material of the cooling vessel | User Input
Vessels | Cooling Vessel Radius | 106.2728 | cm | Outer radius of the cooling vessel | Calculated
Vessels | Cooling Vessel Thickness | 0.5 | cm | Wall thickness of the cooling vessel | User Input
Vessels | Gap Between Cooling Vessel And Intake Vessel | 5 | cm | Radial gap between the cooling vessel and intake vessel | User Input
Vessels | Gap Between Guard Vessel And Cooling Vessel | 5 | cm | Radial gap between the guard vessel and cooling vessel | User Input
Vessels | Gap Between Vessel And Guard Vessel | 5 | cm | Radial gap between the reactor vessel and guard vessel | User Input
Vessels | Guard Vessel Mass | 1871.1608 | kg | Total mass of the guard vessel | Calculated
Vessels | Guard Vessel Material | stainless_steel |  | Structural material of the guard vessel | User Input
Vessels | Guard Vessel Radius | 100.2728 | cm | Outer radius of the guard vessel | Calculated
Vessels | Guard Vessel Thickness | 1 | cm | Wall thickness of the guard vessel (0 if none) | User Input
Vessels | Intake Vessel Mass | 1071.1003 | kg | Total mass of the intake vessel | Calculated
Vessels | Intake Vessel Material | stainless_steel |  | Structural material of the intake vessel | User Input
Vessels | Intake Vessel Radius | 111.7728 | cm | Outer radius of the intake vessel | Calculated
Vessels | Intake Vessel Thickness | 0.5 | cm | Wall thickness of the intake vessel | User Input
Vessels | Total Vessels Mass | 7383.3069 | kg | Combined mass of all vessel components (pressure vessel, guard, cooling, intake) | Calculated
Vessels | Vessel Bottom Depth | 32.129 | cm | Depth of the vessel bottom head (ellipsoidal) | User Input
Vessels | Vessel Height | 306.232 | cm | Total height of the reactor pressure vessel | Calculated
Vessels | Vessel Lower Plenum Height | 50 | cm | Height of the lower plenum region below the active core | User Input
Vessels | Vessel Mass | 3436.5321 | kg | Total mass of the reactor pressure vessel | Calculated
Vessels | Vessel Material | stainless_steel |  | Structural material of the reactor pressure vessel | User Input
Vessels | Vessel Radius | 93.2728 | cm | Inner radius of the reactor pressure vessel (or core barrel) | User Input
Vessels | Vessel Thickness | 2 | cm | Wall thickness of the reactor pressure vessel | User Input
Vessels | Vessel Upper Gas Gap | 0 | cm | Height of the upper gas gap above the upper plenum (0 if none) | User Input
Vessels | Vessel Upper Plenum Height | 47.152 | cm | Height of the upper plenum region above the active core | User Input
Vessels | Vessels Total Height | 356.861 | cm | Total height of the complete vessel assembly | Calculated
Vessels | Vessels Total Radius | 112.2728 | cm | Total outer radius of the complete vessel assembly | Calculated
--- OPERATION ---
Operation | A75: Inner Vessel Structure Replacement Period (cycles) | 2 | cycles | Number of fuel cycles between scheduled inner vessel structure replacements | User Input
Operation | A75: Moderator Booster Replacement Period (cycles) | 1 | cycles | Number of complete fuel cycles between moderator booster replacements | User Input
Operation | A75: Outer Vessel Structure Replacement Period (years) | 20 | years | Service period in years between scheduled outer vessel structure replacements | User Input
Operation | A75: Reactor Control Devices Replacement Period (cycles) | 2 | cycles | Number of fuel cycles between scheduled reactor control device replacements | User Input
Operation | A75: Reflector Replacement Period (cycles) | 2 | cycles | Number of fuel cycles between scheduled reflector replacements | User Input
Operation | A78: CAPEX to Decommissioning Cost Ratio | 0.15 | fraction | Ratio of total decommissioning cost to total capital cost (typical range: 9%–15%) | User Input
Operation | Annual Electricity Production | 53605.2 | MWh/year | Total annual electricity production at the calculated capacity factor | Calculated
Operation | Capacity Factor | 0.98699 | fraction | Annual plant capacity factor — fraction of the year the plant operates at full power | Calculated
Operation | Emergency Shutdowns Per Year | 0.2 | events/year | Expected number of unplanned emergency shutdowns per year | User Input
Operation | Levelization Period | 60 | years | Plant lifetime used for LCOE levelization (economic analysis period) | User Input
Operation | Maintenance to Direct Cost Ratio | 0.03 | fraction | Ratio of annual non-replacement maintenance cost to total direct capital cost | User Input
Operation | Number of On-Site Operators per Shift | 2 |  | Number of concurrent on-site operators assigned per shift | User Input
Operation | Onsite Coolant Inventory | 36660 | kg | Total mass of coolant stored on site (fresh + used tanks) | User Input
Operation | Operation Mode | Remotely Monitored |  | Reactor operation mode: Remotely Monitored, On-Site Staffed, or On-Site Staffed and Remotely Monitored | User Input
Operation | Reactors Monitored Per Operator | 10 |  | Number of reactors that can be monitored by a single operator | User Input
Operation | Refueling Period | 7 | days | Duration of the scheduled refueling outage | User Input
Operation | Replacement Coolant Inventory | 0 | kg | Mass of coolant replaced per refueling cycle | User Input
Operation | Security Staff Per Shift | 1 |  | Number of security personnel required per shift | User Input
Operation | Startup Duration after Emergency Shutdown | 14 | days | Duration of the startup sequence following an emergency shutdown | User Input
Operation | Startup Duration after Refueling | 2 | days | Duration of the startup sequence following a refueling outage | User Input
--- ECONOMIC PARAMETERS ---
Economic Parameters | Annual Return | 0.0475 | fraction | Annual return rate assumed for the decommissioning reserve fund | User Input
Economic Parameters | Assumed Number Of Units For Onsite Learning | 200 |  | Number of units assumed for onsite learning (typically 2 × NOAK Unit Number) | Calculated
Economic Parameters | Construction Duration | 12 | months | Duration of plant construction used for financing cost calculation | User Input
Economic Parameters | Control Building Basement Volume | 5.9448 | m³ | Volume of concrete in the control building basement | User Input
Economic Parameters | Control Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the control building exterior walls | User Input
Economic Parameters | Control Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the control building slab roof | User Input
Economic Parameters | Cost Sampling Seed | 12345 |  | Fixed NumPy random seed used to make cost-uncertainty sampling reproducible across reactor comparisons. | User Input
Economic Parameters | Debt To Equity Ratio | 1 | fraction | Ratio of debt financing to equity financing for the project | User Input
Economic Parameters | Discount Rate | 0.07 | fraction | Annual discount rate (WACC) used for LCOE levelization and cost annualization | User Input
Economic Parameters | Emergency Building Basement Volume | 0 | m³ | Volume of concrete in the emergency building basement (0 if none) | User Input
Economic Parameters | Emergency Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the emergency building exterior walls (0 if none) | User Input
Economic Parameters | Emergency Building Slab Roof Volume | 0 | m³ | Volume of concrete in the emergency building slab roof (0 if none) | User Input
Economic Parameters | Escalation Year | 2025 | year | Reference year to which all costs are escalated for consistent comparison | User Input
Economic Parameters | Excavation Volume | 412.605 | m³ | Volume of earth to be excavated for plant construction | User Input
Economic Parameters | FTEs Per Offsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per offsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator (24/7) | 5 | FTE/operator | Full-time equivalents needed per onsite operator position to maintain 24/7 coverage | User Input
Economic Parameters | FTEs Per Onsite Operator Per Year | 0.017963 | FTE/operator/year | Total FTE-years per operator per year including all activities | Calculated
Economic Parameters | FTEs Per Operator Per Year Per Refueling | 0.0084259 | FTE/operator/year | Fraction of an FTE spent per operator per year on refueling-related activities | User Input
Economic Parameters | FTEs Per Security Staff (24/7) | 5 | FTE/staff | Full-time equivalents needed per security staff position to maintain 24/7 coverage | User Input
Economic Parameters | Hours Per FTE | 1800 | hours/year | Annual working hours per full-time equivalent employee | User Input
Economic Parameters | Integrated Heat Exchanger Building Basement Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building basement (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building exterior walls (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Slab Roof Volume | 0 | m³ | Volume of concrete in the integrated heat exchanger building slab roof (0 if none) | User Input
Economic Parameters | Integrated Heat Exchanger Building Superstructure Area | 0 | m² | Floor area of the integrated heat exchanger building superstructure (0 if none) | User Input
Economic Parameters | Interest Rate | 0.07 | fraction | Annual cost of debt used to calculate interest during construction (Account 62) | User Input
Economic Parameters | Land Area | 18 | acres | Total land area required for the plant site | User Input
Economic Parameters | Manipulator Building Basement Volume | 17.8374 | m³ | Volume of concrete in the manipulator building basement | User Input
Economic Parameters | Manipulator Building Exterior Walls Volume | 15.9195 | m³ | Volume of concrete in the manipulator building exterior walls | User Input
Economic Parameters | Manipulator Building Slab Roof Volume | 4.7566 | m³ | Volume of concrete in the manipulator building slab roof | User Input
Economic Parameters | NOAK Unit Number | 100 |  | Nth-of-a-kind unit number used to calculate the learning curve cost multiplier | User Input
Economic Parameters | Number of Samples | 20 |  | Number of Monte Carlo samples used for cost uncertainty quantification | User Input
Economic Parameters | Radwaste Building Basement Volume | 0 | m³ | Volume of concrete in the radioactive waste building basement (0 if none) | User Input
Economic Parameters | Radwaste Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the radioactive waste building exterior walls (0 if none) | User Input
Economic Parameters | Radwaste Building Slab Roof Volume | 0 | m³ | Volume of concrete in the radioactive waste building slab roof (0 if none) | User Input
Economic Parameters | Reactor Building Basement Volume | 95.0976 | m³ | Volume of concrete in the reactor building basement | User Input
Economic Parameters | Reactor Building Exterior Walls Volume | 129.9564 | m³ | Volume of concrete in the reactor building exterior walls | User Input
Economic Parameters | Reactor Building Slab Roof Volume | 95.0976 | m³ | Volume of concrete in the reactor building slab roof | User Input
Economic Parameters | Reactor Building Superstructure Area | 77 | m² | Floor area of the reactor building superstructure | User Input
Economic Parameters | Refueling Building Basement Volume | 0 | m³ | Volume of concrete in the refueling building basement (0 if none) | User Input
Economic Parameters | Refueling Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the refueling building exterior walls (0 if none) | User Input
Economic Parameters | Refueling Building Slab Roof Volume | 0 | m³ | Volume of concrete in the refueling building slab roof (0 if none) | User Input
Economic Parameters | Spent Fuel Building Basement Volume | 0 | m³ | Volume of concrete in the spent fuel building basement (0 if none) | User Input
Economic Parameters | Spent Fuel Building Exterior Walls Volume | 0 | m³ | Volume of concrete in the spent fuel building exterior walls (0 if none) | User Input
Economic Parameters | Spent Fuel Building Slab Roof Volume | 0 | m³ | Volume of concrete in the spent fuel building slab roof (0 if none) | User Input
Economic Parameters | Storage Building Basement Volume | 11.76 | m³ | Volume of concrete in the storage building basement | User Input
Economic Parameters | Storage Building Exterior Walls Volume | 15.768 | m³ | Volume of concrete in the storage building exterior walls | User Input
Economic Parameters | Storage Building Slab Roof Volume | 11.76 | m³ | Volume of concrete in the storage building slab roof (houses operational spares) | User Input
Economic Parameters | Turbine Building Basement Volume | 5.9448 | m³ | Volume of concrete in the turbine building basement | User Input
Economic Parameters | Turbine Building Exterior Walls Volume | 14.2072 | m³ | Volume of concrete in the turbine building exterior walls | User Input
Economic Parameters | Turbine Building Slab Roof Volume | 5.9448 | m³ | Volume of concrete in the turbine building slab roof | User Input
Economic Parameters | Work Hours Per Shift | 10 | hours | Duration of each work shift | User Input
Economic Parameters | indirect to direct field-related cost | 0.06539 | fraction | Ratio of indirect field (site) costs to total direct field costs — covers site supervision, temporary facilities, and other indirect site activities | User Input
--- LEARNING RATES ---
Learning Rates | Factory Be | 0.41505 | fraction | Learning rate for factory-manufactured beryllium components | User Input
Learning Rates | Factory Be Cost Multiplier | 0.028363 | fraction | NOAK cost multiplier for beryllium components based on Wright's Law | Calculated
Learning Rates | Factory BeO | 0.39915 | fraction | Learning rate for factory-manufactured beryllium oxide components | User Input
Learning Rates | Factory BeO Cost Multiplier | 0.033897 | fraction | NOAK cost multiplier for beryllium oxide components based on Wright's Law | Calculated
Learning Rates | Factory Drums | 0.24138 | fraction | Learning rate for factory-manufactured control drum components | User Input
Learning Rates | Factory Drums Cost Multiplier | 0.15955 | fraction | NOAK cost multiplier for factory-built control drums based on Wright's Law | Calculated
Learning Rates | Factory Other | 0.22963 | fraction | Learning rate for other factory-manufactured components | User Input
Learning Rates | Factory Other Cost Multiplier | 0.17671 | fraction | NOAK cost multiplier for other factory-built components based on Wright's Law | Calculated
Learning Rates | Factory Primary Structure | 0.18443 | fraction | Learning rate for factory-manufactured primary structural components | User Input
Learning Rates | Factory Primary Structure Cost Multiplier | 0.25808 | fraction | NOAK cost multiplier for factory-built primary structure based on Wright's Law | Calculated
Learning Rates | Licensing Learning | 0 | fraction | Learning rate for licensing costs per doubling of cumulative units produced | User Input
Learning Rates | Licensing Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for licensing costs based on Wright's Law | Calculated
Learning Rates | No Learning | 0 | fraction | Learning rate for components with no learning benefit (fixed costs, rate = 0) | User Input
Learning Rates | No Learning Cost Multiplier | 1 | fraction | NOAK cost multiplier for components with no learning (always 1.0) | Calculated
Learning Rates | Non-nuclear off-the-shelf | 0.05 | fraction | Learning rate for non-nuclear commercial off-the-shelf components | User Input
Learning Rates | Non-nuclear off-the-shelf Cost Multiplier | 0.71121 | fraction | NOAK cost multiplier for non-nuclear commercial components based on Wright's Law | Calculated
Learning Rates | Onsite Learning | 0.08 | fraction | Learning rate for onsite construction and installation activities | User Input
Learning Rates | Onsite Learning Cost Multiplier | 0.57466 | fraction | NOAK cost multiplier for onsite construction activities based on Wright's Law | Calculated
--- TAX CREDITS ---
Tax Credits | ITC credit level | 0.3 | fraction | Investment Tax Credit level under IRA Section 48E. Values: 0.06 (base), 0.30 (prevailing wage), 0.40 (+domestic content), 0.50 (+energy community). Applied as a one-time reduction to the Overnight Capital Cost. | User Input
Tax Credits | Number of Units Claiming ITC/PTC | 10 |  | Number of units in the order book that may claim ITC or PTC before the IRA sunset. A unit is eligible only if its position in the deployment sequence is <= this cutoff. FOAK is unit 1; the NOAK column represents unit "NOAK Unit Number". When a unit is past the cutoff, ITC/PTC-adjusted outputs fall back to the un-subsidized values. | User Input
--- DEBUG / INTERMEDIATE VALUES ---
Debug / Intermediate Values | EOL Snapshot Depletion Index | 6 |  | Saved depletion index nearest the estimated end-of-life time and used for the screening EOL temperature-coefficient calculation. | Calculated
Debug / Intermediate Values | Lifecycle Target Times (BOL) | 0 | days | Target lifecycle times before selecting saved depletion compositions. Screening mode reports BOL and estimated EOL; detailed mode also reports half-life. — beginning of life | Calculated
Debug / Intermediate Values | Lifecycle Target Times (EOL) | 1593.1638 | days | Target lifecycle times before selecting saved depletion compositions. Screening mode reports BOL and estimated EOL; detailed mode also reports half-life. — end of life | Calculated
Debug / Intermediate Values | Temperature Coefficient Base Seeds | [104729, 2104732] |  | Independent OpenMC random seeds used for the base-temperature lifecycle snapshots. | Calculated
Debug / Intermediate Values | Temperature Coefficient High Seeds | [15485863, 17485896] |  | Independent OpenMC random seeds used for the elevated-temperature lifecycle snapshots. | Calculated
Debug / Intermediate Values | Temperature Coefficient Particles | [4000, 4000] | particles per batch | Particle counts used for each unique depletion index required by the BOL, MOL, and EOL temperature-coefficient snapshot pairs. | Calculated
Debug / Intermediate Values | Temperature Coefficient Static Depletion Indices | [0, 6] |  | Unique operating depletion indices used for the BOL, MOL, and EOL temperature-coefficient snapshot pairs. | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARI (BOL) | 0.95778 |  | keff at BOL, MOL, and EOL for the cold shutdown configuration, corrected from 2D to 3D using the axial leakage approximation. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARI Uncertainty (BOL) | 0.003235 |  | One standard deviation OpenMC statistical uncertainty for cold shutdown axial-leakage-corrected keff at BOL, MOL, and EOL. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (first) | 1.0956 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — first reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (last) | 0.67457 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — last reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (min) | 0.67457 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO (max) | 1.0956 |  | keff at each burnup step for the operating configuration with all control drums withdrawn (ARO), corrected from 2D to 3D and evaluated at Common Temperature. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (first) | 0.003453 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — first reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (last) | 0.001935 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — last reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (min) | 0.001935 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) ARO Uncertainty (max) | 0.003453 |  | One standard deviation OpenMC statistical uncertainty for axial-leakage-corrected operating keff at each depletion point. Axial leakage model uncertainty is excluded. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (first) | 0.003453 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — first reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (last) | 0.001935 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — last reported value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (min) | 0.001935 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — minimum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) Uncertainty (max) | 0.003453 |  | One standard deviation OpenMC statistical uncertainty for the axial-leakage-corrected operating keff values. Axial leakage model uncertainty is excluded. — maximum value | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp (BOL) | 1.0888 |  | Axial-leakage-corrected keff from the dedicated nominal-temperature ARO static calculations used to evaluate the temperature coefficient at BOL, MOL, and EOL. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp (EOL) | 0.99592 |  | Axial-leakage-corrected keff from the dedicated nominal-temperature ARO static calculations used to evaluate the temperature coefficient at BOL, MOL, and EOL. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp Uncertainty (BOL) | 0.002318 |  | One standard deviation OpenMC statistical uncertainty for the dedicated nominal-temperature axial-leakage-corrected keff values used in the temperature coefficient calculations. Axial leakage model uncertainty is excluded. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) base temp Uncertainty (EOL) | 0.002024 |  | One standard deviation OpenMC statistical uncertainty for the dedicated nominal-temperature axial-leakage-corrected keff values used in the temperature coefficient calculations. Axial leakage model uncertainty is excluded. — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp (BOL) | 1.0902 |  | keff at BOL, MOL, and EOL at elevated temperature corrected to 3D — used to calculate temperature coefficient — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp (EOL) | 0.99609 |  | keff at BOL, MOL, and EOL at elevated temperature corrected to 3D — used to calculate temperature coefficient — end of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp Uncertainty (BOL) | 0.00253 |  | One standard deviation OpenMC statistical uncertainty for elevated-temperature axial-leakage-corrected keff at BOL, MOL, and EOL. — beginning of life | Calculated
Debug / Intermediate Values | keff 3D (2D corrected) high temp Uncertainty (EOL) | 0.002227 |  | One standard deviation OpenMC statistical uncertainty for elevated-temperature axial-leakage-corrected keff at BOL, MOL, and EOL. — end of life | Calculated
--- UNCATEGORIZED ---
Uncategorized | BOL Axial Non-Leakage Probability Used For Shielding | 0.98331 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | BOL Core Leakage Source Rate (n/s) | 76605870034724864 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | BOL Radial Leakage Fraction | 0.03721 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | BOL Total Leakage Fraction Used For Shielding | 0.05328 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Dynamic Shielding Calculation | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Estimated Shutdown Dose Rate (mrem/h) | 0.16751 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Estimated Shutdown Dose Rate Std Dev (mrem/h) | 0.07268 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Leakage Source Radius Outside Intake Vessel (cm) | 112.2728 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Leakage Source Rate Outside Intake Vessel (n/s) | 3107134088608440 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Activation Step Days | 90 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Batches | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Calculation Directory | /home/hannbn/projects/MARVEL_MRP/Github_repos/mice/MOUSE/shielding_runs/run_20260919T070338Z |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Concrete Activation Zone Boundaries | [5.0, 25.0] |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Concrete Thickness | 200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Confirmation Increment | 5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Decay Days | 90 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Detector Distance | 30 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Detector Radius | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Dose Criterion Met | TRUE |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Dose Limit | 0.5 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Initial Upper Thickness | 60 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Irradiation Years | 60 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Maximum Search Iterations | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Maximum Thickness | 200 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Particles | 5000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Batches | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Maximum Retries | 1 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Particles | 50000 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Photon Retry Multiplier | 4 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Pit Clearance | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Temperature | 300 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Thickness Tolerance | 10 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Shielding Working Directory | /home/hannbn/projects/MARVEL_MRP/Github_repos/mice/MOUSE/shielding_runs |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown
Uncategorized | Vessel Neutron Transmission Fraction | 0.04056 |  | --- Not in params registry. Please add to cost/params_registry.py --- | Unknown