## Cost Database
Account | Level | Account Name | Account Title | Fixed Cost ($) | Unit Cost ($) | Unit Cost (units) | Scaling Variable | Scaling Variable Ref Value | Units | Exponent | Dollar Year | Type | Source | Ref | Link | Notes
10 | 0 | Capitalized Pre-Construction Costs | Capitalized Pre-Construction Costs
11 | 1 | Land Cost | Land Cost |  | 3800 | $/acres | Land Area |  | acres |  | 2022 | General | The average cost per acre for rural land in 2022 from the US Department of Agriculture | Abou-Jaoude, A., Lohse, C. S., Larsen, L. M., Guaita, N., Trivedi, I., Joseck, F. C., ... & Stein, A. (2024). Meta-analysis of advanced nuclear reactor cost estimations (No. INL/RPT-24-77048-Rev001). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_107010.pdf
12 | 1 | Site Permits | Site Permits |  | 10030 | $/MWe | Power MWe |  | MWe |  | 2022 | Labor | Data from SMR MHTGRs
13 | 1 | Plant Licensing | Plant Licensing | 50000000 | [6 empty] | 2009 | Labor | NGNP project | Gandrik, A., B. Wallace, L. Demick, S. Melancon and M. Patterson (2011). "Assessment of high temperature gas-cooled reactor (HTGR) capital and operating costs." Idaho National Laboratory, TEV-1196, Idaho Falls, ID. | https://art.inl.gov/NGNP/INL%20Documents/Year%202012/Assessment%20of%20High%20Temperature%20Gas-Cooled%20Reactor%20-%20HTGR%20-%20Capital%20and%20Operating%20Costs.pdf
14 | 1 | Plant Permits | Plant Permits | 3000000 | [6 empty] | 2009 | Labor | NGNP project
15 | 1 | Plant Studies | Plant Studies | 5210451 | [6 empty] | 2024 | Labor | MARVEL Project (Labor-adjusted Cost) | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf | MARVEL's data were updated
20 | 0 | Capitalized Direct Costs | Capitalized Direct Costs
21 | 1 | Structures and Improvements | Structures and Improvements
211 | 2 | Site Preparation/ Yard Work | Site Preparation/ Yard Work
211.1 | 3 | Cleaning and Grubbing | Cleaning and Grubbing |  | 5862.8794 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
211.2 | 3 | Stripping Topsoil | Stripping Topsoil |  | 3411.716 | $/acres | Land Area |  | acres |  | 2024 | Lab and Equip
211.3 | 3 | Excavation | Excavation |  | 32.004 | $/m^3 | Excavation Volume |  | m^3 |  | 2024 | Lab and Equip
212 | 2 | Reactor Island Civil Structures | Reactor Island Civil Structures
212.1 | 3 | Reactor Building Slab Roof | Reactor Building Slab Roof |  | 1836 | $/m^3 | Reactor Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
212.2 | 3 | Reactor Building Basement | Reactor Building Basement |  | 1444.167 | $/m^3 | Reactor Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
212.3 | 3 | Reactor Building Walls | Reactor Building Walls |  | 1103.4513 | $/m^3 | Reactor Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
213 | 2 | Main Function Buildings | Main Function Buildings
213.1 | 3 | Energy conversion Building | Energy conversion Building
213.11 | 4 | Energy Conversion Building Slab Roof | Energy Conversion Building Slab Roof |  | 1836 | $/m^3 | Turbine Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
213.12 | 4 | Energy Conversion Building Basement | Energy Conversion Building Basement |  | 1444.167 | $/m^3 | Turbine Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
213.13 | 4 | Energy Conversion Building Walls | Energy Conversion Building Walls |  | 1103.4513 | $/m^3 | Turbine Building Exterior Wall |  | m^3 |  | 2024 | Lab and Mat and Equip
213.2 | 3 | Control building | Control building
213.21 | 4 | Control Building Slab Roof | Control Building Slab Roof |  | 1836 | $/m^3 | Control Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
213.22 | 4 | Control Building Basement | Control Building Basement |  | 1444.167 | $/m^3 | Control Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
213.23 | 4 | Control Building Walls | Control Building Walls |  | 1103.4513 | $/m^3 | Control Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214 | 2 | Buildings to Support Main Function | Buildings to Support Main Function
214.1 | 3 | Fuel Management Buildings | Fuel Management Buildings
214.11 | 4 | Refueling Building | Refueling Building
214.111 | 5 | Refueling Building Slab Roof | Refueling Building Slab Roof |  | 1836 | $/m^3 | Refueling Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
214.112 | 5 | Refueling Building Basement | Refueling Building Basement |  | 1444.167 | $/m^3 | Refueling Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.113 | 5 | Refueling Building Walls | Refueling Building Walls |  | 1103.4513 | $/m^3 | Refueling Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.12 | 4 | Spent Fuel Building | Spent Fuel Building
214.121 | 5 | Spent Fuel Building Slab Roof | Spent Fuel Building Slab Roof |  | 1836 | $/m^3 | Spent Fuel Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
214.122 | 5 | Spent Fuel Building Basement | Spent Fuel Building Basement |  | 1444.167 | $/m^3 | Spent Fuel Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.123 | 5 | Spent Fuel Building Walls | Spent Fuel Building Walls |  | 1103.4513 | $/m^3 | Spent Fuel Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.7 | 3 | Emergency and Start-up Power Systems Building | Emergency and Start-up Power Systems Building
214.71 | 4 | Emergency Building | Emergency Building
214.711 | 5 | Emergency Building Slab Roof | Emergency Building Slab Roof |  | 1836 | $/m^3 | Emergency Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
214.712 | 5 | Emergency Building Basement | Emergency Building Basement |  | 1444.167 | $/m^3 | Emergency Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.713 | 5 | Emergency Building Walls | Emergency Building Walls |  | 1103.4513 | $/m^3 | Emergency Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
214.72 | 4 | Diesel Generator | Diesel Generator |  | 2653376.4706 | $/MWt | Power MWt | 0.085 | MWt | 0.7 | 2024 | Equipment | MARVEL (for the cost of the diesel generator) The exponent is based on the work by Koruoush considering cost scaling from nuclear ad non nuclear power plants. When using the power as scaling variable, the exponent ranges between 0..6 and 0.8 so 0.7 is used here | Hanna, B. N., Gonzaga de Oliveira, R. G., Mohammad Al Dawood, K. A., Patterson, M. D., Abou Jaoude, A., & Garcia, S. (2024). Technoeconomic Evaluation of Microreactor Using Detailed Bottom-up Estimate (No. INL/RPT-24-80433-Rev000). Idaho National Laboratory (INL), Idaho Falls, ID (United States). Stewart, W. R., & Shirvan, K. (2022). Capital cost estimation for advanced nuclear power plants. Renewable and Sustainable Energy Reviews, 155, 111880. | https://inldigitallibrary.inl.gov/sites/sti/sti/Sort_129862.pdf https://www.sciencedirect.com/science/article/pii/S1364032121011473
215 | 2 | Supply Chain Buildings | Supply Chain Buildings
215.1 | 3 | Storage Building | Storage Building
215.11 | 4 | Storage Building Slab Roof | Storage Building Slab Roof |  | 1836 | $/m^3 | Storage Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
215.12 | 4 | Storage Building Basement | Storage Building Basement |  | 1444.167 | $/m^3 | Storage Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
215.13 | 4 | Storage Building Walls | Storage Building Walls |  | 1103.4513 | $/m^3 | Storage Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
215.4 | 3 | Radwaste Building | Radwaste Building
215.41 | 4 | Radwaste Building Slab Roof | Radwaste Building Slab Roof |  | 1836 | $/m^3 | Radwaste Building Slab Roof Volume |  | m^3 |  | 2024 | Lab and Mat and Equip | RSMeans software: a tool that primarily provides costs for non-nuclear work Nuclear Multiplier have been applied to adjust the costs for nuclear-site-related work | GORDIAN. (2024). "RSMeans data. & Delene, J. G. and I. Hudson, C. R. (1993). Cost estimate guidelines for advanced nuclear power technologies. United States, Oak Ridge National Lab. (ORNL), Oak Ridge, TN (United States): Medium: ED; Size: 159 p. | https://www.rsmeans.com/ & https://www.osti.gov/biblio/10176857
215.42 | 4 | Radwaste Building Basement | Radwaste Building Basement |  | 1444.167 | $/m^3 | Radwaste Building Basement Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
215.43 | 4 | Radwaste Building Walls | Radwaste Building Walls |  | 1103.4513 | $/m^3 | Radwaste Building Exterior Walls Volume |  | m^3 |  | 2024 | Lab and Mat and Equip
22 | 1 | Reactor System | Reactor System
221 | 2 | Reactor Components | Reactor Components
221.1 | 3 | Reactor Vessel and Accessories | Reactor Vessel and Accessories
221.11 | 4 | Reactor Support | Reactor Support
221.12 | 4 | Outer Vessel Structure | Outer Vessel Structure
221.13 | 4 | Inner Vessel Structure | Inner Vessel Structure
221.2 | 3 | Reactor Control Devices | Reactor Control Devices
221.21 | 4 | Reactivity Control System | Reactivity Control System
221.211 | 5 | Reactivity Control System Fabrication | Reactivity Control System Fabrication
221.212 | 5 | Installation | Installation
221.213 | 5 | Control Drums Materials | Control Drums Materials
221.214 | 5 | Control Drums Materials | Control Drums Materials
221.3 | 3 | Non-Fuel Core Internals | Non-Fuel Core Internals
221.31 | 4 | Reflector | Reflector
221.32 | 4 | Shield | Shield
221.321 | 5 | In Vessel Shield Materials | In Vessel Shield Materials
221.322 | 5 | Out The Vessel Shield Materials | Out The Vessel Shield Materials
222 | 2 | Main Heat Transport System | Main Heat Transport System
222.1 | 3 | Fluid Circulation Drive System (Pumps) | Fluid Circulation Drive System (Pumps)
222.11 | 4 | Primary Pumps | Primary Pumps
222.12 | 4 | Secondary Pumps | Secondary Pumps
222.2 | 3 | Reactor Heat Transfer Piping System | Reactor Heat Transfer Piping System
222.3 | 3 | Heat Exchangers | Heat Exchangers
222.31 | 4 | Immediate Heat Exchanger | Immediate Heat Exchanger
222.32 | 4 | Secondary Heat Exchanger | Secondary Heat Exchanger
223 | 2 | Safety Systems | Safety Systems
223.2 | 3 | Reactor Cavity Cooling System (Rvacs) | Reactor Cavity Cooling System (Rvacs)
223.21 | 4 | Rvacs (Cooling Vessel) | Rvacs (Cooling Vessel)
223.22 | 4 | Rvacs (Intake Vessel) | Rvacs (Intake Vessel)
227 | 2 | Reactor Instrumentation and Control (I&C) | Reactor Instrumentation and Control (I&C)
227.1 | 3 | I&C Baseline Cost | I&C Baseline Cost
227.2 | 3 | I&C Autonomous Control | I&C Autonomous Control
23 | 1 | Energy Conversion System | Energy Conversion System
232 | 2 | Energy Applications | Energy Applications
232.1 | 3 | Electricity Generation Systems (Turbines) | Electricity Generation Systems (Turbines)
24 | 1 | Electrical Equipment | Electrical Equipment
25 | 1 | Initial Fuel Inventory | Initial Fuel Inventory
251 | 2 | First Core Mining | First Core Mining
252 | 2 | First Core Conversion | First Core Conversion
253 | 2 | First Core Enrichment | First Core Enrichment
254 | 2 | First Core Fuel Assembly Fabrication | First Core Fuel Assembly Fabrication
254.1 | 3 | Fuel Production and Procurement | Fuel Production and Procurement
254.1 | 3 | Other Related Activities | Other Related Activities
26 | 1 | Miscellaneous Equipment (Cranes) | Miscellaneous Equipment (Cranes)
30 | 0 | Capitalized Indirect Services Cost | Capitalized Indirect Services Cost
31 | 1 | Factory & Field Indirect Costs | Factory & Field Indirect Costs
32 | 1 | Factory & Construction Supervision | Factory & Construction Supervision
33 | 1 | Startup Costs | Startup Costs
34 | 1 | Shipping and Transportation Costs | Shipping and Transportation Costs
35 | 1 | Engineering Services | Engineering Services
36 | 1 | Pm/Cm Services | Pm/Cm Services
60 | 0 | Capitalized Financial Costs | Capitalized Financial Costs
62 | 1 | Interest | Interest
70 | 0 | Annualized O&M Cost | Annualized O&M Cost
71 | 1 | O&M Staff | O&M Staff
711 | 2 | Operators | Operators
712 | 2 | Remote Monitoring Technicians | Remote Monitoring Technicians
713 | 2 | Security Staff | Security Staff
75 | 1 | Capital Plant Expenditures | Capital Plant Expenditures
78 | 1 | Annualized Decommissioning Cost | Annualized Decommissioning Cost
80 | 0 | Annualized Fuel Cost | Annualized Fuel Cost
81 | 1 | Refueling Operations | Refueling Operations
82 | 1 | Additional Nuclear Fuel | Additional Nuclear Fuel
83 | 1 | Spent Fuel Management | Spent Fuel Management
Overnight Capital Cost (OCC)
OCC ($/kW)
OCC Excluding Fuel ($/kW)
Total Capital Investment (TCI)
TCI ($/kW)
Annualized Cost ($/ year)
Annualized Cost ($/MWh)
Levelized Cost Of Energy (LCOE) ($/MWh)

## Inflation Adjustment
Year | General | Labor | Material | Equipment | Lab and Mat and Equip | Lab and Equip
1985 | 2.4641 | 3.1849 | 3.0545 | 3.8306 | 3.3566 | 3.5077
1986 | 2.4153 | 3.0852 | 3.0607 | 3.7331 | 3.293 | 3.4092
1987 | 2.3571 | 2.9916 | 2.9992 | 3.6991 | 3.23 | 3.3453
1988 | 2.2768 | 2.8748 | 2.8406 | 3.5246 | 3.08 | 3.1997
1989 | 2.1908 | 2.7813 | 2.7498 | 3.3127 | 2.9479 | 3.047
1990 | 2.1116 | 2.6589 | 2.7466 | 3.2241 | 2.8765 | 2.9415
1991 | 2.0426 | 2.554 | 2.7291 | 3.1182 | 2.8004 | 2.8361
1992 | 1.9972 | 2.4751 | 2.6817 | 2.99 | 2.7156 | 2.7325
1993 | 1.9509 | 2.3964 | 2.5547 | 2.8241 | 2.5917 | 2.6102
1994 | 1.9101 | 2.3109 | 2.4545 | 2.7417 | 2.5024 | 2.5263
1995 | 1.8708 | 2.2707 | 2.3663 | 2.6949 | 2.4439 | 2.4828
1996 | 1.8373 | 2.215 | 2.3528 | 2.6375 | 2.4018 | 2.4263
1997 | 1.8061 | 2.1583 | 2.3124 | 2.576 | 2.3489 | 2.3671
1998 | 1.786 | 2.0934 | 2.3237 | 2.5207 | 2.3126 | 2.3071
1999 | 1.7611 | 2.024 | 2.3013 | 2.5047 | 2.2767 | 2.2644
2000 | 1.7221 | 1.9301 | 2.2793 | 2.4782 | 2.2292 | 2.2042
2001 | 1.6841 | 1.8435 | 2.3007 | 2.3994 | 2.1812 | 2.1214
2002 | 1.6583 | 1.783 | 2.2814 | 2.3771 | 2.1472 | 2.08
2003 | 1.6263 | 1.7217 | 2.2333 | 2.3372 | 2.0974 | 2.0294
2004 | 1.5838 | 1.6722 | 2.0346 | 2.2508 | 1.9859 | 1.9615
2005 | 1.5356 | 1.6186 | 1.9376 | 2.163 | 1.9064 | 1.8908
2006 | 1.4896 | 1.566 | 1.8228 | 1.9965 | 1.7951 | 1.7813
2007 | 1.4503 | 1.5071 | 1.7936 | 1.8327 | 1.7111 | 1.6699
2008 | 1.4228 | 1.455 | 1.6724 | 1.7874 | 1.6383 | 1.6212
2009 | 1.4141 | 1.4394 | 1.7367 | 1.7643 | 1.6468 | 1.6018
2010 | 1.3972 | 1.424 | 1.6891 | 1.7753 | 1.6295 | 1.5996
2011 | 1.3689 | 1.409 | 1.6335 | 1.7021 | 1.5815 | 1.5555
2012 | 1.3439 | 1.387 | 1.5962 | 1.5912 | 1.5248 | 1.4891
2013 | 1.3214 | 1.3588 | 1.5699 | 1.5349 | 1.4879 | 1.4469
2014 | 1.2988 | 1.3395 | 1.532 | 1.4777 | 1.4497 | 1.4086
2015 | 1.2868 | 1.312 | 1.5385 | 1.4366 | 1.4291 | 1.3743
2016 | 1.2747 | 1.2847 | 1.536 | 1.4153 | 1.412 | 1.35
2017 | 1.2523 | 1.2535 | 1.4823 | 1.3824 | 1.3727 | 1.318
2018 | 1.2243 | 1.2201 | 1.3936 | 1.3336 | 1.3157 | 1.2768
2019 | 1.2041 | 1.1832 | 1.3937 | 1.3 | 1.2923 | 1.2416
2020 | 1.1885 | 1.1509 | 1.3736 | 1.2822 | 1.2689 | 1.2165
2021 | 1.1365 | 1.1172 | 1.0828 | 1.2259 | 1.142 | 1.1715
2022 | 1.0616 | 1.0737 | 0.96194 | 1.0847 | 1.0401 | 1.0792
2023 | 1.0242 | 1.0296 | 0.99021 | 1.0049 | 1.0082 | 1.0172
2024 | 1 | 1 | 1 | 1 | 1 | 1